## Cover Sheet
Phase Specification
PH_C_BH
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-001612 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 杜林茂 | 2021-4-12 |  | 杜林茂
Morimatsu approved: | 张蓉蓉 | 2021-4-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_.....
| Step | max. 16 characters, _ for delimiter
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-25 | 杜林茂 | Draft
杜林茂
杜林茂
杜林茂
| 0.1a | 2020-10-28 | 杜林茂 | Updated according to comments
| 0.1a | 2020-10-29 | 杜林茂
| 0.1a | 2020-10-30 | 杜林茂
| 0.1b | 2020-11-10 | 杜林茂 | 1. Description: 更新6. Description 2. 2. SFC_RUN： S1010删除计时报警； S1020更新计时报警参数名称； S1040增加计时报警； 3. Action Table： S7000，S8000中EM_BCIP_CIPS 对应Command修改； 更新S1020中Alarm Settings； S1040增加Alarm Settings； Note11中PH_C_DSXTA17对应处改为N/A 4. ParameterHold Tables： 增加参数R_WFI_TOC_SP； 更新R_MAX_TM_STEP1-4描述; 删除R_Flow_SP_CIPR，增加L_FLOW_CIPR_PV
| 0.1c | 2020-11-20 | 杜林茂 | 1. SFC_HOLD_ABORT: 删除S7000和S8000 2. Action Table: 增加选项参数名称； 更新S1090对应EM_C_RTN中Command； 删除S7000和S8000，并在S7010和S8010增加Other Actions； 将ABORT中Command改为CLOSE 3. ParameterHold Tables：增加选项参数
| 0.1d | 2020-12-09 | 杜林茂 | 1. SFC_RUN: WFI清洗检测策略修改，电导与TOC同时检测，见顺控图； 增加Note2&3 2. Action Table： 更新S1040，S1050 3. ParameterHold Tables: 增加R_TM_DELAY和R_MAX_TM_STEP2； 更新R_TM_CT和R_TM_TOC设定值
| 1.0 | 2021-03-03 | 杜林茂 | 根据仿真测试修改
| 2.0 | 2021-04-12 | 杜林茂 | 增加急停编号

## Description
6. | Description
The Phase C_BH is used for CIP BH tank. Phase at CIP object performs control actions for cleaning of CIP object and controls CIP return pump.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| BH Tank | 3000L BUFFER HOLDING TANK UNIT TA16
3000L BUFFER HOLDING TANK UNIT TA17
3000L BUFFER HOLDING TANK UNIT TA18
3000L BUFFER HOLDING TANK UNIT TA19
3000L PROCESS WATER TANK UNIT TA20
3000L BUFFER HOLDING TANK UNIT TA21
3000L BUFFER HOLDING TANK UNIT TA22
3000L BUFFER HOLDING TANK UNIT TA23
3000L BUFFER HOLDING TANK UNIT TA24
6000L BUFFER HOLDING TANK UNIT TA26
6000L BUFFER HOLDING TANK UNIT TA27
6000L BUFFER HOLDING TANK UNIT TA28
6000L BUFFER HOLDING TANK UNIT TA29
3000L BUFFER HOLDING TANK UNIT TA30
6000L BUFFER HOLDING TANK UNIT TA31
9000L 0.5M NaOH TANK UNIT TA32
9000L BUFFER HOLDING TANK UNIT TA33
9000L BUFFER HOLDING TANK UNIT TA34
9000L BUFFER HOLDING TANK UNIT TA35
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| BH Tank | EM_BH_TOP
EM_BH_HEAD
EM_BH_BOM
EM_BH_FA
EM_BUF_CIPS
EM_BUF_CIPR
EM_BUF_CIPR_PU
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| CIP Station | EM_C_CIP
EM_C_SUP
EM_C_RTN
EM_C_BTH
EM_BCIP_CIPS
EM_BCIP_CIPR

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | RUN Logic with Check Steps
| Note1: | R_SELECT_STATION is 03 or 05. Default of R_SELECT_STATION can be modified.
If R_SELECT_STATION is 03, select CIP03 if CIP03 is standby. Select CIP05 if CIP03 is occupied.

## SFC_RUN
8. | RUN Logic with Check Steps
Note1: | Current Medium will be judged by the logic,according to the parameter CIP_Medium1/CIP_Medium2/CIP_Medium3/CIP_Medium4
Note2 | CHECK_Ct and CHECK_TOC finished
Note3 | Check CT and TOC simultaneously at the start of S1070.
For CHECK_CT:
1) If AIT03 > R_WFI_CT_SP, then CHECK_CT=FAILED. If AIT03 < R_WFI_CT_SP, then enable Timer R_TM_CT.
2) If AIT03 < R_WFI_CT_SP and R_TM_CT is elapsed, then CHECK_CT=PASSED.
If AIT03 > R_WFI_CT_SP during R_TM_CT, then CHECK_CT=FAILED.
For CHECK_TOC:
1) If QIT01 > R_WFI_TOC_SP, then CHECK_TOC=FAILED. If QIT01 < R_WFI_TOC_SP, then enable Timer R_TM_TOC.
2) If QIT01 < R_WFI_TOC_SP and R_TM_TOC is elapsed, then CHECK_TOC=PASSED.
If QIT01 > R_WFI_TOC_SP during R_TM_TOC, then CHECK_TOC=FAILED.
Alarm if CHECK_CT=FAILED or CHECK_TOC=FAILED.
预留TOC检测功能，该phase须能保证在无TOC检测的情况下正常运行。

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution.
| Unit Class | Phase
| Buffer Holding System | PH_C_DSXTA32 | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note10) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | EM_DSXBH1_CIPS | EM_DSXTA32_HEAD | EM_DSXTA32_TOP | EM_DSXTA32_FA | EM_DSXTA32_BOM | EM_DSXBH1_CIPR | EM_DSXBH1_CIPRPU | EM_DSXCIP03_CIPR/EM_DSXCIP05_CIPR (Note4) | EM_DSXCIP03_RTN/EM_DSXCIP05_RTN (Note5)
|  | PH_C_DSXTA33 | [5 empty] | EM_DSXTA33_HEAD | EM_DSXTA33_TOP | EM_DSXTA33_FA | EM_DSXTA33_BOM
|  | PH_C_DSXTA34 | [5 empty] | EM_DSXTA34_HEAD | EM_DSXTA34_TOP | EM_DSXTA34_FA | EM_DSXTA34_BOM
|  | PH_C_DSXTA35 | [5 empty] | EM_DSXTA35_HEAD | EM_DSXTA35_TOP | EM_DSXTA35_FA | EM_DSXTA35_BOM
|  | PH_C_DSXTA26 |  |  |  |  | EM_DSXBH2_CIPS | EM_DSXTA26_HEAD | EM_DSXTA26_TOP | EM_DSXTA26_FA | EM_DSXTA26_BOM | EM_DSXBH2_CIPR | EM_DSXBH2_CIPRPU
|  | PH_C_DSXTA27 | [5 empty] | EM_DSXTA27_HEAD | EM_DSXTA27_TOP | EM_DSXTA27_FA | EM_DSXTA27_BOM
|  | PH_C_DSXTA28 | [5 empty] | EM_DSXTA28_HEAD | EM_DSXTA28_TOP | EM_DSXTA28_FA | EM_DSXTA28_BOM
|  | PH_C_DSXTA29 | [5 empty] | EM_DSXTA29_HEAD | EM_DSXTA29_TOP | EM_DSXTA29_FA | EM_DSXTA29_BOM
|  | PH_C_DSXTA31 | [5 empty] | EM_DSXTA31_HEAD | EM_DSXTA31_TOP | EM_DSXTA31_FA | EM_DSXTA31_BOM
|  | PH_C_DSXTA16 |  |  |  |  | EM_DSXBH3_CIPS | EM_DSXTA16_HEAD | EM_DSXTA16_TOP | EM_DSXTA16_FA | EM_DSXTA16_BOM | EM_DSXBH3_CIPR | EM_DSXBH3_CIPRPU
|  | PH_C_DSXTA18 | [5 empty] | EM_DSXTA18_HEAD | EM_DSXTA18_TOP | EM_DSXTA18_FA | EM_DSXTA18_BOM
|  | PH_C_DSXTA22 | [5 empty] | EM_DSXTA22_HEAD | EM_DSXTA22_TOP | EM_DSXTA22_FA | EM_DSXTA22_BOM
|  | PH_C_DSXTA24 | [5 empty] | EM_DSXTA24_HEAD | EM_DSXTA24_TOP | EM_DSXTA24_FA | EM_DSXTA24_BOM
|  | PH_C_DSXTA20 | [5 empty] | EM_DSXTA20_HEAD | EM_DSXTA20_TOP | EM_DSXTA20_FA | EM_DSXTA20_BOM
|  | PH_C_DSXTA17 |  |  |  |  | EM_DSXBH4_CIPS | EM_DSXTA17_HEAD | EM_DSXTA17_TOP | EM_DSXTA17_FA | EM_DSXTA17_BOM | EM_DSXBH4_CIPR | EM_DSXBH4_CIPRPU
|  | PH_C_DSXTA19 | [5 empty] | EM_DSXTA19_HEAD | EM_DSXTA19_TOP | EM_DSXTA19_FA | EM_DSXTA19_BOM
|  | PH_C_DSXTA21 | [5 empty] | EM_DSXTA21_HEAD | EM_DSXTA21_TOP | EM_DSXTA21_FA | EM_DSXTA21_BOM
|  | PH_C_DSXTA23 | [5 empty] | EM_DSXTA23_HEAD | EM_DSXTA23_TOP | EM_DSXTA23_FA | EM_DSXTA23_BOM
|  | PH_C_DSXTA30 | [5 empty] | EM_DSXTA30_HEAD | EM_DSXTA30_TOP | EM_DSXTA30_FA | EM_DSXTA30_BOM
Step |  | Description | EM_C_CIP | EM_C_SUP | EM_C_BTH | EM_BCIP_CIPS | EM_BUF_CIPS | EM_BH_HEAD | EM_BH_TOP | EM_BH_FA | EM_BH_BOM | EM_BUF_CIPR | EM_BUF_CIPR_PU | EM_BCIP_CIPR | EM_C_RTN | Report Record | Alarm Settings | Controller Settings | Other Actions
S9000 | STATION_CHECK | 检查CIP站的占用状态 Check the occupation of CIP stations. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | MESSAGE | 提示是否放弃 Prompt to abort the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | STATE_CHECK | 状态检查 Check all line and vessel status | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the R_ase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ROUTE_CHECK | 路径检查 Check if all the jumpers are in right position | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9080 | ENABLE HM&SM | 启动程序监测 Enable hold monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S2010 | DEACTIVE | 程序非自结束 Deactive | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | CHECK_MEDIUM | 检查介质 Check medium | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  | Assign value to Current_Medium according to the parameter CIP_Medium1/CIP_Medium2/CIP_Medium3/CIP_Medium4
S1020 | PREP_MEDIUM | 准备介质 CIP station medium preparation | Note6 | STOP | WT_FILTER_OPEN | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | CLOSE | STOP |  | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP1
S1030 | CIP_TK | 清洗喷淋球 CIP tank by spray ball | Note7 | MEDIUM_SUPPLY | WT_FILTER_OPEN | Note8 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | CIP_TK | Note12 | PU_ON | Note13 | Note9
S1040 | CHECK_CT_TOC | 电导和TOC检测 Check CT and TOC | Note7 | MEDIUM_SUPPLY | WT_FILTER_OPEN | Note8 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | CIP_TK | Note12 | PU_ON | Note13 | RTN_TOC | Record AIT03 Record QIT01 |  |  | If Medium is WFI, record AIT03 and QIT01 at the start of S1040. Record result of S1070: CHECK_CT=PASSED or FAILED CHECK_TOC=PASSED or FAILED
S1060 | STOP_PUMP | 停泵 Stop CIPR pump | STOP_PUMP | MEDIUM_SUPPLY | WT_FILTER_OPEN | Note8 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | CIP_TK | Note12 | STOP | Note13 | Note9
S1070 | BLOW_TK | 吹扫喷淋球 Blow tank by spray ball | STOP | AIR_BLOW | WT_FILTER_OPEN | Note8 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | CIP_TK | Note12 | STOP | Note13 | Note9
S1080 | FINAL_CHECK | 最终确认 Check final medium. | STOP | STOP | WT_FILTER_OPEN | Note8 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | CIP_TK | Note12 | STOP | Note13 | Note9
S1090 | BLOW_LP | 吹扫低点 Blow low point | STOP | AIRBLOW_LP | WT_FILTER_OPEN | Note8 | Note11 | CIP_TK | CIP_TK | WFI_PA_FA | CIP_TK_PUL_DRN | Note12 | PU_OFF_DRN | Note13 | RTN_LP_DR
S1100 | CLOSE | 关闭所有设备 Close all device | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | \ | STOP | CLOSE | STOP |  |  |  | If CHECK_CT&CHECK_TOC=PASSED, go to S1110. If CHECK_CT&CHECK_TOC=FAILED, end the phase.
S1110 | SET_STATE | 重置状态 Set state | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | CLOSE | CLOSE |  |  |  | Set state to CLEAN
S7010 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD |  |  |  | First to HOLD EM_C_CIP and EM_BUF_CIPR_PU, then ohrers
S8010 | ABORT | 中止步骤 Abort | STOP | CLOSE | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | CLOSE | CLOSE |  |  |  | First to STOP EM_C_CIP and EM_BUF_CIPR_PU, then ohrers
S8020 | SET_STATE | 重置状态 Set state | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | CLOSE | CLOSE |  |  |  | Set state to DIRTY
Note1: If select CIP03 station, EM will be EM_DSXCIP03. If select CIP05 station, EM will be EM_DSXCIP05.
Note2: If select CIP03 station, EM will be EM_DSXCIP03_SUP. If select CIP05 station, EM will be EM_DSXCIP05_SUP. | [5 empty] | Unit Class | Phase | Note8 | Note11 | Note12 | Note13
Note3: If select CIP03 station, EM will be EM_DSXCIP03_CIPS. If select CIP05 station, EM will be EM_DSXCIP05_CIPS. | [5 empty] | Buffer Holding System | R_C_DSXTA32_SEL | CIP_TO_TA35 | CIP_TO_TA32 | CIPR_FR_TA32 | CIP_FR_TA35
Note4: If select CIP03 station, EM will be EM_DSXCIP03_CIPR. If select CIP05 station, EM will be EM_DSXCIP05_CIPR. | [6 empty] | R_C_DSXTA33_SEL |  | CIP_TO_TA33 | CIPR_FR_TA33
Note5: If select CIP03 station, EM will be EM_DSXCIP03_RTN. If select CIP05 station, EM will be EM_DSXCIP05_RTN. | [6 empty] | R_C_DSXTA34_SEL |  | CIP_TO_TA34 | CIPR_FR_TA34
Note6: If medium is PW, use PREP_PW. If medium is CAU, use PREP_ALK. If medium is WFI, use PREP_WFI. | [6 empty] | R_C_DSXTA35_SEL |  | N/A | N/A
Note7: If medium is PW, use SUPPLY_PW. If medium is CAU, use SUPPLY_ALK. If medium is WFI, use SUPPLU_WFI. | [6 empty] | R_C_DSXTA26_SEL | CIP_TO_TA31 | CIP_TO_TA26 | CIPR_FR_TA26 | CIP_FR_TA31
Note9: If medium is PW, use RTN_DR. If medium is CAU, use RTN_TK. If medium is WFI, use RTN_TOC. | [6 empty] | R_C_DSXTA27_SEL |  | CIP_TO_TA27 | CIPR_FR_TA27
Note10: If select CIP03 station, EM will be EM_DSXCIP03_BTH. If select CIP05 station, EM will be EM_DSXCIP05_BTH. | [6 empty] | R_C_DSXTA28_SEL |  | CIP_TO_TA28 | CIPR_FR_TA28
"X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4. | [6 empty] | R_C_DSXTA29_SEL |  | CIP_TO_TA29 | CIPR_FR_TA29
[7 empty] | R_C_DSXTA31_SEL |  | N/A | N/A
[7 empty] | R_C_DSXTA16_SEL | CIP_TO_TA16 | N/A | N/A | CIP_FR_TA16
[7 empty] | R_C_DSXTA18_SEL |  | CIP_TO_TA18 | CIPR_FR_TA18
[7 empty] | R_C_DSXTA22_SEL |  | CIP_TO_TA22 | CIPR_FR_TA22
[7 empty] | R_C_DSXTA24_SEL |  | CIP_TO_TA24 | CIPR_FR_TA24
[7 empty] | R_C_DSXTA20_SEL |  | CIP_TO_TA20 | CIPR_FR_TA20
[7 empty] | R_C_DSXTA17_SEL | CIP_TO_TA17 | N/A | N/A | CIP_FR_TA17
[7 empty] | R_C_DSXTA19_SEL |  | CIP_TO_TA19 | CIPR_FR_TA19
[7 empty] | R_C_DSXTA21_SEL |  | CIP_TO_TA21 | CIPR_FR_TA21
[7 empty] | R_C_DSXTA23_SEL |  | CIP_TO_TA23 | CIPR_FR_TA23
[7 empty] | R_C_DSXTA30_SEL |  | CIP_TO_TA30 | CIPR_FR_TA30

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| CIP_Medium1 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_Medium2 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_Medium3 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_Medium4 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| R_SELECT_STATION | NO | Preferred CIP Station selected | N/A | N/A | CIP03 or CIP05 | N/A | N/A
| R_TM_CIP_PW | YES | CIP time for tank | real | min | 5 | 1 | 60
| R_TM_CIP_ALK | YES | CIP time for tank | real | min | 20 | 1 | 60
| R_TM_CIP_WFI | YES | CIP time for tank | real | min | 10 | 1 | 60
| R_TM_CT | NO | Conductivity check duration | int | sec | 60 | 1 | 600
| R_TM_TOC | NO | TOC check duration | int | sec | 30 | 1 | 600
| R_TM_BLOW_P | YES | Blow time after PW or ALK flush | real | min | 5 | 1 | 10
| R_TM_BLOW_LP | YES | Blow time after WFI flush | real | min | 5 | 1 | 10
| R_MAX_TM_STEP1 | NO | Maximum step execution time for PREP_MEDIUM, hold if exceed the time | real | min | 30 | 0 | 120
| R_WFI_CT_SP | NO | Qualified CT | real | µS/cm | 1.3 | 0 | 5
| R_WFI_TOC_SP | YES | TOC judgment setpoint | real | ppm | 1 | 1 | 300
| R_Speed_SUP_PU | YES | Speed of supply pump | real | Hz | 35 | 0 | 60
| R_Speed_RTN_PU | NO | Speed of return pump | real | Hz | 35 | 0 | 60
| R_ALK_TEMP | YES | Alkali temperature | real | °C | 80 | 0 | 100
| R_ALK_TM | YES | Alkali preparation time | int | sec | 20 | 0 | 100
| R_ALK_PRE_CT | YES | Alkali preparation CT | real | mS/cm | 18 | 0 | 30
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_WFI_CT_PV |  | Process value of conductivity recorded | real | µS/cm | 1040
| L_WFI_TOC_PV |  | Process value of TOC recorded | real | ppm | 1040
| L_CT_CHECK |  | CHECK_CT is PASSED or FAILED | Nameset | N/A | 1040
| L_TOC_CHECK |  | CHECK_TOC is PASSED or FAILED | Nameset | N/A | 1040
| FE-DSXCIP0301/FE-DSXCIP0501 |  | CIP supply pump flowrate curve | real | m3/h
| AIT-DSXCIP0303/AIT-DSXCIP0503 |  | Conductivity curve during WFI flush | real | µS/cm
| QIT-DSXCIP0301/QIT-DSXCIP0501 |  | TOC curve during WFI flush | real | ppm
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXBH01/E-DS1XCIP02 Emergency Stop
| Hold03 |  | CIP station Hold
| Hold04 |  | R_MAX_TM_STEP is elapsed

## ALARM (hidden)
INDICATION | S150~S180