## Cover Sheet
Phase Specification PH_X_BH_PUR
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-001631 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-04-12 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-04-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-25 | 刘会莹 | Draft
| 0.1a | 2020-10-29 | 刘会莹 | Update according to comments
| 0.1b | 2020-11-20 | 刘会莹 | 修改Stop数控图，删除stop步骤
| 0.1c | 2020-12-10 | 杜林茂 | Action Table：增加EM_BH_POU
| 1.0 | 2021-03-03 | 杜林茂 | 根据程序仿真修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号

## Description
6. | Description
The Phase PH_X_BH_PUR is used for transferring buffer from Buffer holding tank to Process Tank.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class |  | Units
| Process Tank(DPS) |  | 4000L PURIFICATION TANK UNIT TA03 | UF0301
|  |  | 4000L PURIFICATION TANK UNIT TA04 | UF0302
|  |  | 4000L PURIFICATION TANK UNIT TA05 | UF0303
3000L PURIFICATION TANK UNIT TA06
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit |  | Equiment Module
| 4000L PURIFICATION TANK UNIT TA03 | UF0301 | EM_PUR_PD_IN | EM_PUR_TOP | EM_PUR_FA1
| 4000L PURIFICATION TANK UNIT TA04 | UF0302 | EM_PUR_PD_IN | EM_PUR_TOP | EM_PUR_FA1
| 4000L PURIFICATION TANK UNIT TA05 | UF0303 | EM_PUR_PD_IN | EM_PUR_TOP | EM_PUR_FA1
| 3000L PURIFICATION TANK UNIT TA06 |  | EM_PUR_PD_IN | EM_PUR_TOP | EM_PUR_FA1

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN
8. | RUN Logic without Check Steps
|  | Phase | Note 1 | Note 2 | Note 3
|  | Phase：TA20_TO_TA03 | WT_DSXTA0301 | CT_DSXTA0301 | PH_DSXTA0301
|  | Phase：TA21_TO_TA03 | WT_DSXTA0301 | CT_DSXTA0301 | PH_DSXTA0301
|  | Phase：TA20_TO_TA04 | WT_DSXTA0401 | CT_DSXTA0401 | PH_DSXTA0401
|  | Phase：TA29_TO_TA04 | WT_DSXTA0401 | CT_DSXTA0401 | PH_DSXTA0401
|  | Phase：TA35_TO_TA05 | WT_DSXTA0501 | CT_DSXTA0501 | PH_DSXTA0501
|  | Phase：TA30_TO_TA06 | WT_DSXTA0601 | CT_DSXTA0601 | PH_DSXTA0601
R_BF_SP为计算值，不算recipe input参数，改为BUF_WIT

## SFC_HOLD_ABORT_STOP
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
|  | Phase | EM
|  | Phase: TA20_TO_TA03 | EM_DSXTA20_TA03 | EM_DSXTA03_PD_IN | EM_DSXTA03_TOP | EM_DSXTA03_FA
|  | Phase: TA21_TO_TA03 | N/A | EM_DSXTA03_PD_IN | EM_DSXTA03_TOP | EM_DSXTA03_FA
|  | Phase: TA20_TO_TA04 | EM_DSXTA20_TA04 | EM_DSXTA04_PD_IN | EM_DSXTA04_TOP | EM_DSXTA04_FA
|  | Phase:TA29_TO_TA04 | N/A | EM_DSXTA04_PD_IN | EM_DSXTA04_TOP | EM_DSXTA04_FA
|  | Phase:TA35_TO_TA05 | N/A | EM_DSXTA05_PD_IN | EM_DSXTA05_TOP | EM_DSXTA05_FA
|  | Phase:TA30_TO_TA06 | N/A | EM_DSXTA06_PD_IN | EM_DSXTA06_TOP | EM_DSXTA06_FA
Step |  | Description | EM_BH_POU | EM_PUR_PD_IN | EM_PUR_TOP | EM_PUR_FA1 | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 check if all the EM are free or not | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 prompt to continue or complete the phase | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A
S1010 | WT_CHECK | 计算缓冲液需求添加量。 Calculate buffer quantity required. | N/A | N/A | N/A | N/A
S1020 | BUFFER_SUP | 缓冲液转移到用点 Buffer supply to point of use | BUF_OUT | Note1 | PD_IN | VENT_FA
S1030 | FILL_UP | 缓冲液定容到目标值 Buffer fill up | BUF_OUT | Note1 | PD_IN_PUL | VENT_FA
S1040 | WT_CHECK | 计算缓冲液实际添加量。 Calculate buffer actual quantity. | CLOSE | CLOSE | CLOSE | CLOSE
S1050 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE
S1060 | SET_STATE | 状态变更 Set State | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Target Tank = Process Line State = Dirty
S7010 | HOLD | 暂停 pause | HOLD | HOLD | HOLD | HOLD
S8010 | ABORT | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE
S8020 | SET_STATE | 状态变更 Set State | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Target Tank = Process Line State = Process
|  | Phase | Note1
|  | Phase：TA20_TO_TA03 | WFI_TO_TK
|  | Phase：TA21_TO_TA03 | BUF_TO_TK
|  | Phase：TA20_TO_TA04 | WFI_TO_TK
|  | Phase：TA29_TO_TA04 | BUF_TO_TK
|  | Phase：TA35_TO_TA05 | BUF_TO_TK
|  | Phase：TA30_TO_TA06 | BUF_TO_TK

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_X | Yes | Ratio X for buffer quantity calculation | Real | N/A | 1 | 0 | 100
| R_WT_DEV | Yes | Constant volume weight | Real | kg | 5 | 0 | 1000
| R_PH_SP | Yes | Purification Tank PH set point | Real | N/A | 7 | 0 | 14
| R_PH_SP_DEV | Yes | Purification Tank PH Deviation | Real | N/A | 0.1 | 0 | 7
| R_CT_SP | Yes | Purification Tank conductivity set point | Real | mS/cm | 10 | 0 | 1000
| R_CT_SP_DEV | Yes | Purification Tank conductivity Deviation | Real | mS/cm | 2 | 0 | 100
| R_PH_SP | Yes | Purification Tank PH set point | Real | N/A | 7 | 1 | 14
| R_PH_SP_DEV | Yes | Purification Tank PH Deviation | Real | N/A | 0.2 | 1 | 14
| R_DELAY_TM | No | Delay timer for Agitator | Real | min | 5 | 0 | 100
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_CT_PV |  | Purification Tank conductivity | Real
| L_PH_PV |  | Purification Tank PH | Real
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXBH01 Emergency Stop
| Hold04 |  | Weightometer of purification tank fault

## ALARM (hidden)
INDICATION | S150~S180