## Cover Sheet
Phase Specification
PH_S_BP_BH
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-001636 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-04-12 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-04-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-25 | 刘会莹 | Draft
| 0.1a | 2020-10-29 | 刘会莹 | Update according to comments
| 0.1b | 2020-11-02 | 刘会莹 | Update according to comments
| 0.1c | 2020-11-17 | 刘会莹 | Update according to comments
| 0.1d | 2020-11-20 | 刘会莹 | 删除abort里的close命令
| 0.1e | 2020-12-10 | 杜林茂 | ParameterHold Tables：更新HOLD Table
| 1.0 | 2021-03-03 | 王树深 | 程序仿真修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号

## Description
6. | Description
The Phase PH_S_BP_BH is used for Sterilization of transfer pipe from Buffer Preparation Tank to Buffer holding tank. 1. Monitoring of all condensate temperatures in sterilization step and resetting of sterilization timer if one of the temperatures drop SIP_SET_TT.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| BP Tank | 9000L BUFFER PREPARATION TANK UNIT TA15
6000L BUFFER PREPARATION TANK UNIT TA14
3000L BUFFER PREPARATION TANK UNIT TA13
3000L BUFFER PREPARATION TANK UNIT TA12
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| BP Tank | EM_BUF_CS
EM_BP_TOP
EM_BP_HEAD
EM_BP_BOM
EM_BP_DIS
EM_TP01_DIS
EM_TP02_DIS
EM_BH_TOP
EM_BP_SU

## SFC_CHECK
8. | SFC Check Steps for RUN Logic
note:1
|  | SIP_TA15_BH | CS_SEL1: | from TA15 toTA32 | ZS-DSXTP0101=1
|  |  | CS_SEL2: | from TA15 toTA33 | ZS-DSXTP0102=1
|  |  | CS_SEL3: | from TA15 toTA34 | ZS-DSXTP0103=1
|  |  | CS_SEL4: | from TA15 toTA35 | ZS-DSXTP0104=1
|  |  | CS_SEL5: | from TA15 toTA26 | ZS-DSXTP0205=1
|  |  | CS_SEL6: | from TA15 toTA27 | ZS-DSXTP0206=1
|  |  | CS_SEL7: | from TA15 toTA28 | ZS-DSXTP0207=1
|  |  | CS_SEL8: | from TA15 toTA29 | ZS-DSXTP0208=1
|  |  | CS_SEL9: | from TA15 toTA31 | ZS-DSXTP0209=1
|  | SIP_TA14_BH | CS_SEL1: | from TA14 toTA32 | ZS-DSXTP0101=1 | ZS-DSXTP0244=1
|  |  | CS_SEL2: | from TA14 toTA33 | ZS-DSXTP0102=1 | ZS-DSXTP0244=1
|  |  | CS_SEL3: | from TA14 toTA34 | ZS-DSXTP0103=1 | ZS-DSXTP0244=1
|  |  | CS_SEL4: | from TA14 toTA35 | ZS-DSXTP0104=1 | ZS-DSXTP0244=1
|  |  | CS_SEL5: | from TA14 toTA26 | ZS-DSXTP0210=1
|  |  | CS_SEL6: | from TA14 toTA27 | ZS-DSXTP0211=1
|  |  | CS_SEL7: | from TA14 toTA28 | ZS-DSXTP0212=1
|  |  | CS_SEL8: | from TA14 toTA29 | ZS-DSXTP0213=1
|  |  | CS_SEL9: | from TA14 toTA31 | ZS-DSXTP0214=1
|  |  | CS_SEL10: | from TA14 toTA16 | ZS-DSXTP0315=1
|  |  | CS_SEL11: | from TA14 toTA18 | ZS-DSXTP0316=1
|  |  | CS_SEL12: | from TA14 toTA22 | ZS-DSXTP0317=1
|  |  | CS_SEL13: | from TA14 toTA24 | ZS-DSXTP0318=1
|  |  | CS_SEL14: | from TA14 toTA17 | ZS-DSXTP0319=1
|  |  | CS_SEL15: | from TA14 toTA19 | ZS-DSXTP0320=1
|  |  | CS_SEL16: | from TA14 toTA21 | ZS-DSXTP0321=1
|  |  | CS_SEL17: | from TA14 toTA23 | ZS-DSXTP0322=1
|  |  | CS_SEL18: | from TA14 toTA30 | ZS-DSXTP0323=1
|  | SIP_TA13_BH | CS_SEL1: | from TA13 toTA26 | ZS-DSXTP0210=1 | ZS-DSXTP0345=1
|  |  | CS_SEL2: | from TA13 toTA27 | ZS-DSXTP0211=1 | ZS-DSXTP0345=1
|  |  | CS_SEL3: | from TA13 toTA28 | ZS-DSXTP0212=1 | ZS-DSXTP0345=1
|  |  | CS_SEL4: | from TA13 toTA29 | ZS-DSXTP0213=1 | ZS-DSXTP0345=1
|  |  | CS_SEL5: | from TA13 toTA31 | ZS-DSXTP0214=1 | ZS-DSXTP0345=1
|  |  | CS_SEL6: | from TA13 toTA16 | ZS-DSXTP0324=1
|  |  | CS_SEL7: | from TA13 toTA18 | ZS-DSXTP0325=1
|  |  | CS_SEL8: | from TA13 toTA22 | ZS-DSXTP0326=1
|  |  | CS_SEL9: | from TA13 toTA24 | ZS-DSXTP0327=1
|  |  | CS_SEL10: | from TA13 toTA17 | ZS-DSXTP0328=1
|  |  | CS_SEL11: | from TA13 toTA19 | ZS-DSXTP0329=1
|  |  | CS_SEL12: | from TA13 toTA21 | ZS-DSXTP0330=1
|  |  | CS_SEL13: | from TA13 toTA23 | ZS-DSXTP0331=1
|  |  | CS_SEL14: | from TA13 toTA30 | ZS-DSXTP0332=1
|  |  | CS_SEL15: | from TA13 to SUBAG | ZS-DSXTP0333=1
|  | SIP_TA12_BH | CS_SEL1: | from TA12 toTA26 | ZS-DSXTP0210=1 | ZS-DSXTP0346=1
|  |  | CS_SEL2: | from TA12 toTA27 | ZS-DSXTP0211=1 | ZS-DSXTP0346=1
|  |  | CS_SEL3: | from TA12 toTA28 | ZS-DSXTP0212=1 | ZS-DSXTP0346=1
|  |  | CS_SEL4: | from TA12 toTA29 | ZS-DSXTP0213=1 | ZS-DSXTP0346=1
|  |  | CS_SEL5: | from TA12 toTA31 | ZS-DSXTP0214=1 | ZS-DSXTP0346=1
|  |  | CS_SEL6: | from TA12 toTA16 | ZS-DSXTP0334=1
|  |  | CS_SEL7: | from TA12 toTA18 | ZS-DSXTP0335=1
|  |  | CS_SEL8: | from TA12 toTA22 | ZS-DSXTP0336=1
|  |  | CS_SEL9: | from TA12 toTA24 | ZS-DSXTP0337=1
|  |  | CS_SEL10: | from TA12 toTA17 | ZS-DSXTP0338=1
|  |  | CS_SEL11: | from TA12 toTA19 | ZS-DSXTP0339=1
|  |  | CS_SEL12: | from TA12 toTA21 | ZS-DSXTP0340=1
|  |  | CS_SEL13: | from TA12 toTA23 | ZS-DSXTP0341=1
|  |  | CS_SEL14: | from TA12 toTA30 | ZS-DSXTP0342=1
|  |  | CS_SEL15: | from TA12 to SUBAG | ZS-DSXTP0343=1

## SFC_RUN
8. | RUN Logic without Check Steps
Note2:
|  | SIP_TA15_BH | CS_SEL1: | from TA15 toTA32 | TT means TT-DSXTA1504B/TT-DSXTA1511/TT-DSXTA1512/TT-DSXTA1514/TT-DSXTA1513/TT-DSXTA1515/TT-DSXTA3203A
|  |  | CS_SEL2: | from TA15 toTA33 | TT means TT-DSXTA1504B/TT-DSXTA1511/TT-DSXTA1512/TT-DSXTA1514/TT-DSXTA1513/TT-DSXTA1515/TT-DSXTA3203B
|  |  | CS_SEL3: | from TA15 toTA34 | TT means TT-DSXTA1504B/TT-DSXTA1511/TT-DSXTA1512/TT-DSXTA1514/TT-DSXTA1513/TT-DSXTA1515/TT-DSXTA3403A
|  |  | CS_SEL4: | from TA15 toTA35 | TT means TT-DSXTA1504B/TT-DSXTA1511/TT-DSXTA1512/TT-DSXTA1514/TT-DSXTA1513/TT-DSXTA1515/TT-DSXTA3403B
|  |  | CS_SEL5: | from TA15 toTA26 | TT means TT-DSXTA1504B/TT-DSXTA1511/TT-DSXTA1512/TT-DSXTA1514/TT-DSXTA1513/TT-DSXTA1515/TT-DSXTA2603A
|  |  | CS_SEL6: | from TA15 toTA27 | TT means TT-DSXTA1504B/TT-DSXTA1511/TT-DSXTA1512/TT-DSXTA1514/TT-DSXTA1513/TT-DSXTA1515/TT-DSXTA2603B
|  |  | CS_SEL7: | from TA15 toTA28 | TT means TT-DSXTA1504B/TT-DSXTA1511/TT-DSXTA1512/TT-DSXTA1514/TT-DSXTA1513/TT-DSXTA1515/TT-DSXTA2803A
|  |  | CS_SEL8: | from TA15 toTA29 | TT means TT-DSXTA1504B/TT-DSXTA1511/TT-DSXTA1512/TT-DSXTA1514/TT-DSXTA1513/TT-DSXTA1515/TT-DSXTA2803B
|  |  | CS_SEL9: | from TA15 toTA31 | TT means TT-DSXTA1504B/TT-DSXTA1511/TT-DSXTA1512/TT-DSXTA1514/TT-DSXTA1513/TT-DSXTA1515/TT-DSXTA3103A
|  | SIP_TA14_BH | CS_SEL1: | from TA14 toTA32 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA3203A
|  |  | CS_SEL2: | from TA14 toTA33 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA3203B
|  |  | CS_SEL3: | from TA14 toTA34 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA3403A
|  |  | CS_SEL4: | from TA14 toTA35 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA3403B
|  |  | CS_SEL5: | from TA14 toTA26 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA2603A
|  |  | CS_SEL6: | from TA14 toTA27 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA2603B
|  |  | CS_SEL7: | from TA14 toTA28 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA2803A
|  |  | CS_SEL8: | from TA14 toTA29 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA2803B
|  |  | CS_SEL9: | from TA14 toTA31 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA3103A
|  |  | CS_SEL10: | from TA14 toTA16 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA1603A
|  |  | CS_SEL11: | from TA14 toTA18 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA1603B
|  |  | CS_SEL12: | from TA14 toTA22 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA2203A
|  |  | CS_SEL13: | from TA14 toTA24 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA2203B
|  |  | CS_SEL14: | from TA14 toTA17 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA1703A
|  |  | CS_SEL15: | from TA14 toTA19 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA1703B
|  |  | CS_SEL16: | from TA14 toTA21 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA2103A
|  |  | CS_SEL17: | from TA14 toTA23 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA2103B
|  |  | CS_SEL18: | from TA14 toTA30 | TT means TT-DSXTA1504C/TT-DSXTA1406/TT-DSXTA1407/TT-DSXTA1409/TT-DSXTA1408/TT-DSXTA1410/TT-DSXTA3003A
|  | SIP_TA13_BH | CS_SEL1: | from TA13 toTA26 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA2603A
|  |  | CS_SEL2: | from TA13 toTA27 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA2603B
|  |  | CS_SEL3: | from TA13 toTA28 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA2803A
|  |  | CS_SEL4: | from TA13 toTA29 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA2803B
|  |  | CS_SEL5: | from TA13 toTA31 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA3103A
|  |  | CS_SEL6: | from TA13 toTA16 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA1603A
|  |  | CS_SEL7: | from TA13 toTA18 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA1603B
|  |  | CS_SEL8: | from TA13 toTA22 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA2203A
|  |  | CS_SEL9: | from TA13 toTA24 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA2203B
|  |  | CS_SEL10: | from TA13 toTA17 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA1703A
|  |  | CS_SEL11: | from TA13 toTA19 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA1703B
|  |  | CS_SEL12: | from TA13 toTA21 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA2103A
|  |  | CS_SEL13: | from TA13 toTA23 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA2103B
|  |  | CS_SEL14: | from TA13 toTA30 | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA2103B
|  |  | CS_SEL15: | from TA13 to subag | TT means TT-DSXTA1304B/TT-DSXTA1316/TT-DSXTA1317/TT-DSXTA1320/TT-DSXTA1318/TT-DSXTA1319/TT-DSXTA1321
|  | SIP_TA13_BH | CS_SEL1: | from TA12 toTA26 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA2603A
|  |  | CS_SEL2: | from TA12 toTA27 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA2603B
|  |  | CS_SEL3: | from TA12 toTA28 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA2803A
|  |  | CS_SEL4: | from TA12 toTA29 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA2803B
|  |  | CS_SEL5: | from TA12 toTA31 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA3103A
|  |  | CS_SEL6: | from TA12 toTA16 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA1603A
|  |  | CS_SEL7: | from TA12 toTA18 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA1603B
|  |  | CS_SEL8: | from TA12 toTA22 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA2203A
|  |  | CS_SEL9: | from TA12 toTA24 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA2203B
|  |  | CS_SEL10: | from TA12 toTA17 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA1703A
|  |  | CS_SEL11: | from TA12 toTA19 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA1703B
|  |  | CS_SEL12: | from TA12 toTA21 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA2103A
|  |  | CS_SEL13: | from TA12 toTA23 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA2103B
|  |  | CS_SEL14: | from TA12 toTA30 | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA3003A
|  |  | CS_SEL15: | from TA12 to subag | TT means TT-DSXTA1304C/TT-DSXTA1201/TT-DSXTA1202/TT-DSXTA1204/TT-DSXTA1203/TT-DSXTA1205/TT-DSXTA1321
|  | SIP_TA15_BH | CS_SEL10: | TA15 WFI pipe SIP | TT means TT-DSXTA1503B
|  | SIP_TA14_BH | CS_SEL19: | TA14 WFI pipe SIP | TT means TT-DSXTA1503C
|  | SIP_TA13_BH | CS_SEL16: | TA13 WFI pipe SIP | TT means TT-DSXTA1303B
|  | SIP_TA12_BH | CS_SEL16: | TA12 WFI pipe SIP | TT means TT-DSXTA1303C

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## ALARM (hidden)
INDICATION | S150~S180

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Phase(Note3) |  |  | EM
Phase:SIP_TA15_BH |  | CS_SEL1:from TA15 toTA32 | EM_DSXBP_CS | N/A | EM_DSXTA15_HEAD | EM_DSXTA15_BOM | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | EM_DSXTA32_TOP | N/A
Phase:SIP_TA15_BH |  | CS_SEL2:from TA15 toTA33 | EM_DSXBP_CS | N/A | EM_DSXTA15_HEAD | EM_DSXTA15_BOM | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | EM_DSXTA33_TOP | N/A
Phase:SIP_TA15_BH |  | CS_SEL3:from TA15 toTA34 | EM_DSXBP_CS | N/A | EM_DSXTA15_HEAD | EM_DSXTA15_BOM | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | EM_DSXTA34_TOP | N/A
Phase:SIP_TA15_BH |  | CS_SEL4:from TA15 toTA35 | EM_DSXBP_CS | N/A | EM_DSXTA15_HEAD | EM_DSXTA15_BOM | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | EM_DSXTA35_TOP | N/A
Phase:SIP_TA15_BH |  | CS_SEL5:from TA15 toTA26 | EM_DSXBP_CS | N/A | EM_DSXTA15_HEAD | EM_DSXTA15_BOM | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | EM_DSXTA26_TOP | N/A
Phase:SIP_TA15_BH |  | CS_SEL6:from TA15 toTA27 | EM_DSXBP_CS | N/A | EM_DSXTA15_HEAD | EM_DSXTA15_BOM | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | EM_DSXTA27_TOP | N/A
Phase:SIP_TA15_BH |  | CS_SEL7:from TA15 toTA28 | EM_DSXBP_CS | N/A | EM_DSXTA15_HEAD | EM_DSXTA15_BOM | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | EM_DSXTA28_TOP | N/A
Phase:SIP_TA15_BH |  | CS_SEL8:from TA15 toTA29 | EM_DSXBP_CS | N/A | EM_DSXTA15_HEAD | EM_DSXTA15_BOM | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | EM_DSXTA29_TOP | N/A
Phase:SIP_TA15_BH |  | CS_SEL9:from TA15 toTA31 | EM_DSXBP_CS | N/A | EM_DSXTA15_HEAD | EM_DSXTA15_BOM | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | EM_DSXTA31_TOP | N/A
Phase:SIP_TA15_BH |  | CS_SEL10:TA15 WFI IN SIP | EM_DSXBP_CS | EM_DSXTA15_TOP | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phase:SIP_TA14_BH |  | CS_SEL1:from TA14 toTA32 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | EM_DSXTP01_DIS | EM_DSXTP02_DIS | EM_DSXTA32_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL2:from TA14 toTA33 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | EM_DSXTP01_DIS | EM_DSXTP02_DIS | EM_DSXTA33_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL3:from TA14 toTA34 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | EM_DSXTP01_DIS | EM_DSXTP02_DIS | EM_DSXTA34_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL4:from TA14 toTA35 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | EM_DSXTP01_DIS | EM_DSXTP02_DIS | EM_DSXTA35_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL5:from TA14 toTA26 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA26_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL6:from TA14 toTA27 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA27_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL7:from TA14 toTA28 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA28_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL8:from TA14 toTA29 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA29_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL9:from TA14 toTA31 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA31_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL10:from TA14 toTA16 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA16_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL11:from TA14 toTA18 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA18_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL12:from TA14 toTA22 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA22_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL13:from TA14 toTA24 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA24_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL14:from TA14 toTA17 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA17_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL15:from TA14 toTA19 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA19_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL16:from TA14 toTA21 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA21_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL17:from TA14 toTA23 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA23_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL18:from TA14 toTA30 | EM_DSXBP_CS | N/A | EM_DSXTA14_HEAD | EM_DSXTA14_BOM | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA30_TOP | N/A
Phase:SIP_TA14_BH |  | CS_SEL19:TA14 WFI IN SIP | EM_DSXBP_CS | EM_DSXTA14_TOP | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phase:SIP_TA13_BH |  | CS_SEL1:from TA13 toTA26 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA26_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL2:from TA13 toTA27 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA27_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL3:from TA13 toTA28 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA28_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL4:from TA13 toTA29 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA29_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL5:from TA13 toTA31 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA31_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL6:from TA13 toTA16 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | EM_DSXTA16_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL7:from TA13 toTA18 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | EM_DSXTA18_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL8:from TA13 toTA22 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | EM_DSXTA22_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL9:from TA13 toTA24 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | EM_DSXTA24_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL10:from TA13 toTA17 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | EM_DSXTA17_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL11:from TA13 toTA19 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | EM_DSXTA19_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL12:from TA13 toTA21 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | EM_DSXTA21_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL13:from TA13 toTA23 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | EM_DSXTA23_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL14:from TA13 toTA30 | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | EM_DSXTA30_TOP | N/A
Phase:SIP_TA13_BH |  | CS_SEL15:from TA13 to subag | EM_DSXBP_CS | N/A | EM_DSXTA13_HEAD | EM_DSXTA13_BOM | EM_DSXTA13_DIS | N/A | N/A | N/A | EM_DSXBP_SU
Phase:SIP_TA13_BH |  | CS_SEL16:TA13 WFI IN SIP | EM_DSXBP_CS | EM_DSXTA13_TOP | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phase:SIP_TA12_BH |  | CS_SEL1:from TA12 toTA26 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA26_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL2:from TA12 toTA27 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA27_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL3:from TA12 toTA28 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA28_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL4:from TA12 toTA29 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA29_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL5:from TA12 toTA31 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS | EM_DSXTA31_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL6:from TA12 toTA16 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | EM_DSXTA16_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL7:from TA12 toTA18 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | EM_DSXTA18_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL8:from TA12 toTA22 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | EM_DSXTA22_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL9:from TA12 toTA24 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | EM_DSXTA24_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL10:from TA12 toTA17 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | EM_DSXTA17_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL11:from TA12 toTA19 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | EM_DSXTA19_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL12:from TA12 toTA21 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | EM_DSXTA21_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL13:from TA12 toTA23 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | EM_DSXTA23_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL14:from TA12 toTA30 | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | EM_DSXTA30_TOP | N/A
Phase:SIP_TA12_BH |  | CS_SEL15:from TA12 to subag | EM_DSXBP_CS | N/A | EM_DSXTA12_HEAD | EM_DSXTA12_BOM | EM_DSXTA12_DIS | N/A | N/A | N/A | EM_DSXBP_SU
Phase:SIP_TA12_BH |  | CS_SEL16:TA12 WFI IN SIP | EM_DSXBP_CS | EM_DSXTA12_TOP | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Step |  | Description | EM_BUF_CS | EM_BP_TOP | EM_BP_HEAD | EM_BP_BOM | EM_BP_DIS | EM_TP01_DIS | EM_TP02_DIS | EM_BH_TOP | EM_BP_SU | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | PRE-HEAT | 管道通入纯蒸汽加热，打开排放旁路，排除凝水，管道继续升温。 Heat pipe by clean steam and DRNain condensate water by bypass valve. | CS_SUPPLY_DIS | SIP_WFI_PE | SIP_PE | SIP_PE | SIP_FILT_HEAT | Note1 | Note2 | SIP_BPS | SIP_BPS | Enable "HM" if TT <R_HEAT_TT_SP when Step_Timer is over | SP: EM_DSXBP_CS_PIC OUT= R_CS_PT_SP1
S1020 | HEAT | 管道通入纯蒸汽加热，只通过疏水阀排除凝水，罐体继续升温。 Heat pipe by clean steam and DRNain by steam trap valve. | CS_SUPPLY_DIS | SIP_WFI_PE | SIP_PE | SIP_PE | SIP_FILT_HEAT | Note1 | Note2 | SIP_PD_IN_PE | SIP_PE | Enable "HM" if TT <R_SIP_TT_SP when Step_Timer is over | SP: EM_DSXBP_CS_PIC OUT= R_CS_PT_SP2
S1030 | STERILIZE | 灭菌计时 Sterilize timer. | CS_SUPPLY_DIS | SIP_WFI_PE | SIP_PE | SIP_PE | SIP_FILT | Note1 | Note2 | SIP_PD_IN_PE | SIP_PE
S1040 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Release EM:EM_DSXBP_CS
S1050 | SET_STATE | 状态变更 Set State | N/A | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Change the state to SIPed
S1200 | REHEAT | 重新加热通过加入纯蒸汽。 Reheat tank by into clean stean. | CS_SUPPLY_DIS | SIP_WFI_PE | SIP_PE | SIP_PE | SIP_FILT | Note1 | Note2 | SIP_PD_IN_PE | SIP_PE |  | SP: EM_BUF_CS_PIC OUT= R_CS_PT_SP1
S7000 | HOLD | 暂停 pause | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD
S8010 | ABORT | 关闭所有阀门。 Close all valve. | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Release EM:EM_DSXBP_CS
S8020 | SET_STATE | 状态变更 Set State | N/A | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Change the state to Clean.
| Description | Note1 | Note2
| CS_SEL1:from TA15 toTA32 | BUF_TS | N/A
| CS_SEL2:from TA15 toTA33 | BUF_TS | N/A
| CS_SEL3:from TA15 toTA34 | BUF_TS | N/A
| CS_SEL4:from TA15 toTA35 | BUF_TS | N/A
| CS_SEL5:from TA15 toTA26 | BUF_TS_1 | N/A
| CS_SEL6:from TA15 toTA27 | BUF_TS_1 | N/A
| CS_SEL7:from TA15 toTA28 | BUF_TS_1 | N/A
| CS_SEL8:from TA15 toTA29 | BUF_TS_1 | N/A
| CS_SEL9:from TA15 toTA31 | BUF_TS_1 | N/A
| CS_SEL10:TA15 WFI IN SIP | N/A | N/A
| CS_SEL1:from TA14 toTA32 | BUF_TS_2 | BUF_TS
| CS_SEL2:from TA14 toTA33 | BUF_TS_2 | BUF_TS
| CS_SEL3:from TA14 toTA34 | BUF_TS_2 | BUF_TS
| CS_SEL4:from TA14 toTA35 | BUF_TS_2 | BUF_TS
| CS_SEL5:from TA14 toTA26 | N/A | BUF_TS
| CS_SEL6:from TA14 toTA27 | N/A | BUF_TS
| CS_SEL7:from TA14 toTA28 | N/A | BUF_TS
| CS_SEL8:from TA14 toTA29 | N/A | BUF_TS
| CS_SEL9:from TA14 toTA31 | N/A | BUF_TS
| CS_SEL10:from TA14 toTA16 | N/A | BUF_TS_1
| CS_SEL11:from TA14 toTA18 | N/A | BUF_TS_1
| CS_SEL12:from TA14 toTA22 | N/A | BUF_TS_1
| CS_SEL13:from TA14 toTA24 | N/A | BUF_TS_1
| CS_SEL14:from TA14 toTA17 | N/A | BUF_TS_1
| CS_SEL15:from TA14 toTA19 | N/A | BUF_TS_1
| CS_SEL16:from TA14 toTA21 | N/A | BUF_TS_1
| CS_SEL17:from TA14 toTA23 | N/A | BUF_TS_1
| CS_SEL18:from TA14 toTA30 | N/A | BUF_TS_1
| CS_SEL19:TA14 WFI IN SIP | N/A | N/A
| CS_SEL1:from TA13 toTA26 | N/A | BUF_TS_2
| CS_SEL2:from TA13 toTA27 | N/A | BUF_TS_2
| CS_SEL3:from TA13 toTA28 | N/A | BUF_TS_2
| CS_SEL4:from TA13 toTA29 | N/A | BUF_TS_2
| CS_SEL5:from TA13 toTA31 | N/A | BUF_TS_2
| CS_SEL6:from TA13 toTA16 | N/A | N/A
| CS_SEL7:from TA13 toTA18 | N/A | N/A
| CS_SEL8:from TA13 toTA22 | N/A | N/A
| CS_SEL9:from TA13 toTA24 | N/A | N/A
| CS_SEL10:from TA13 toTA17 | N/A | N/A
| CS_SEL11:from TA13 toTA19 | N/A | N/A
| CS_SEL12:from TA13 toTA21 | N/A | N/A
| CS_SEL13:from TA13 toTA23 | N/A | N/A
| CS_SEL14:from TA13 toTA30 | N/A | N/A
| CS_SEL15:from TA13 to subag | N/A | N/A
| CS_SEL16:TA13 WFI IN SIP | N/A | N/A
| CS_SEL1:from TA12 toTA26 | N/A | BUF_TS_2
| CS_SEL2:from TA12 toTA27 | N/A | BUF_TS_2
| CS_SEL3:from TA12 toTA28 | N/A | BUF_TS_2
| CS_SEL4:from TA12 toTA29 | N/A | BUF_TS_2
| CS_SEL5:from TA12 toTA31 | N/A | BUF_TS_2
| CS_SEL6:from TA12 toTA16 | N/A | N/A
| CS_SEL7:from TA12 toTA18 | N/A | N/A
| CS_SEL8:from TA12 toTA22 | N/A | N/A
| CS_SEL9:from TA12 toTA24 | N/A | N/A
| CS_SEL10:from TA12 toTA17 | N/A | N/A
| CS_SEL11:from TA12 toTA19 | N/A | N/A
| CS_SEL12:from TA12 toTA21 | N/A | N/A
| CS_SEL13:from TA12 toTA23 | N/A | N/A
| CS_SEL14:from TA12 toTA30 | N/A | N/A
| CS_SEL15:from TA12 to subag | N/A | N/A
| CS_SEL16:TA12 WFI IN SIP | N/A | N/A
Note3：All the phases existed in DS1/DS2/DS3/DS4.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_CS_PT_SP1 | YES | Steam pressure set point for pre-heating pipe | Real | barg | 1.5 | 0 | 2.5
| R_CS_PT_SP2 | YES | Steam pressure set point for sterilize pipe | Real | barg | 1.1 | 0 | 2.5
| R_S1010_STEP_TM | NO | maximum pre-heating time,hold if exceed the time | Real | min | 20 | 2 | 100
| R_S1020_STEP_TM | NO | maximum heating time,hold if exceed the time | Real | min | 20 | 5 | 100
| R_HEAT_TT_SP | Yes | temperature set point for pre-heating | Real | °C | 95 | 80 | 100
| R_SIP_TT_SP | YES | SIP control temperature | Real | °C | 123 | 121 | 125
| R_SIP_TT_SP_DEV | NO | SIP temperature Deviation | Real | °C | 1 | 0 | 99
| R_STABLE_TM | NO | Stable time | Real | min | 2 | 0 | 10
| R_SIP_TM | YES | SIP time | Real | min | 30 | 0 | 60
| R_TA15_BH_S_SEL | YES | Pipe from TA15 toTA32 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA15 toTA33 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA15 toTA34 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA15 toTA35 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA15 toTA26 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA15 toTA27 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA15 toTA28 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA15 toTA29 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA15 toTA31 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA15 WFI IN SIP | N/A | N/A | N/A | N/A | N/A
| R_TA14_BH_S_SEL | YES | Pipe from TA14 toTA32 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA33 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA34 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA35 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA26 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA27 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA28 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA29 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA31 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA16 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA18 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA22 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA24 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA17 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA19 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA21 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA23 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA14 toTA30 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA14 WFI IN SIP | N/A | N/A | N/A | N/A | N/A
| R_TA13_BH_S_SEL | YES | Pipe from TA13 toTA26 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA27 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA28 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA29 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA31 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA16 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA18 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA22 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA24 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA17 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA19 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA21 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA23 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA13 toTA30 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe fromA13 to subag | N/A | N/A | N/A | N/A | N/A
|  | YES | TA13 WFI IN SIP | N/A | N/A | N/A | N/A | N/A
| R_TA12_BH_S_SEL | YES | Pipe from TA12 toTA26 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA27 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA28 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA29 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA31 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA16 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA18 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA22 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA24 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA17 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA19 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA21 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA23 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe from TA12 toTA30 | N/A | N/A | N/A | N/A | N/A
|  | YES | Pipe fromA12 to subag | N/A | N/A | N/A | N/A | N/A
|  | YES | TA12 WFI IN SIP | N/A | N/A | N/A | N/A | N/A
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase Pipe from The defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_SIP_TT_PV |  | Report SIP temperature | Real | ℃ | S1030 | N/A | N/A
| L_SIP_TM |  | Report SIP time | Real | min | S1030 | N/A | N/A
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXBP01/E-DSXBH01 Emergency Stop
| Hold03 |  | Step timer S1010,S1020 elapsed
| Hold04 |  | Any TT fault