## Cover Sheet
Phase Specification
PH_S_BUF
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-001637 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-4-12 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-4-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-25 | 刘会莹 | Draft
| 0.1a | 2020-10-29 | 刘会莹 | update according to comments
| 0.1b | 2020-11-09 | 刘会莹 | Update according to comments
| 0.1c | 2020-12-10 | 杜林茂 | ParameterHold Tables： 更新HOLD Table
| 1.0 | 2021-03-03 | 王树深 | 程序仿真修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号

## Description
6. | Description
The Phase PH_S_BUF is used for Sterilization of tank with cooling by chilled water; tank heated by plant steam 1. Monitoring of all condensate temperatures in sterilization step and resetting of sterilization timer if one of the temperatures drop SIP_SET_TT.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| BP Tank | 9000L BUFFER PREPARATION TANK UNIT TA15
6000L BUFFER PREPARATION TANK UNIT TA14
3000L BUFFER PREPARATION TANK UNIT TA13
3000L BUFFER PREPARATION TANK UNIT TA12
| BH Tank | 3000L BUFFER HOLDING TANK UNIT TA16
3000L BUFFER HOLDING TANK UNIT TA17
3000L BUFFER HOLDING TANK UNIT TA18
3000L BUFFER HOLDING TANK UNIT TA19
3000L PROCESS WATER TANK UNIT TA20
3000L BUFFER HOLDING TANK UNIT TA21
3000L BUFFER HOLDING TANK UNIT TA22
3000L BUFFER HOLDING TANK UNIT TA23
3000L BUFFER HOLDING TANK UNIT TA24
6000L BUFFER HOLDING TANK UNIT TA26
6000L BUFFER HOLDING TANK UNIT TA27
6000L BUFFER HOLDING TANK UNIT TA28
6000L BUFFER HOLDING TANK UNIT TA29
3000L BUFFER HOLDING TANK UNIT TA30
6000L BUFFER HOLDING TANK UNIT TA31
9000L 0.5M NaOH TANK UNIT TA32
9000L BUFFER HOLDING TANK UNIT TA33
9000L BUFFER HOLDING TANK UNIT TA34
9000L BUFFER HOLDING TANK UNIT TA35
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| BP Tank | EM_BUF_CS
EM_BUF_PS
EM_BUF_JC
EM_BP_FA
EM_BP_HEAD
EM_BP_TOP
EM_BP_BOM
| BH Tank | EM_BUF_CS
EM_BUF_PS
EM_BUF_JC
EM_BH_FA
EM_BH_HEAD
EM_BH_TOP
EM_BH_BOM

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN
8. | RUN Logic without Check Steps
|  | Unit class | Phase | TT(Note1): | TT(Note2): |  |  | PT(Note3):
|  | Buffer Prep Tank | Phase:SIP_TA13 | TT-DSXTA1201B | TT-DSXTA1201B | TT-DSXTA1203B | TT-DSXTA1204B | PT-DSXTA1201B
|  |  | Phase:SIP_TA12 | TT-DSXTA1201C | TT-DSXTA1201C | TT-DSXTA1203C | TT-DSXTA1204C | PT-DSXTA1201C
|  |  | Phase:SIP_TA15 | TT-DSXTA1501B | TT-DSXTA1501B | TT-DSXTA1503B | TT-DSXTA1504B | PT-DSXTA1501B
|  |  | Phase:SIP_TA14 | TT-DSXTA1501C | TT-DSXTA1501C | TT-DSXTA1503C | TT-DSXTA1504C | PT-DSXTA1501C
|  | Buffer Hold Tank | Phase:SIP_TA32 | TT-DSXTA3201A | TT-DSXTA3201A | TT-DSXTA3205A | TT-DSXTA3204A | PT-DSXTA3201A
|  |  | Phase:SIP_TA33 | TT-DSXTA3201B | TT-DSXTA3201B | TT-DSXTA3205B | TT-DSXTA3204B | PT-DSXTA3201B
|  |  | Phase:SIP_TA34 | TT-DSXTA3401A | TT-DSXTA3401A | TT-DSXTA3405A | TT-DSXTA3404A | PT-DSXTA3401A
|  |  | Phase:SIP_TA35 | TT-DSXTA3401B | TT-DSXTA3401B | TT-DSXTA3405B | TT-DSXTA3404B | PT-DSXTA3401B
|  |  | Phase:SIP_TA26 | TT-DSXTA2601A | TT-DSXTA2601A | TT-DSXTA2605A | TT-DSXTA2604A | PT-DSXTA2601A
|  |  | Phase:SIP_TA27 | TT-DSXTA2601B | TT-DSXTA2601B | TT-DSXTA2605B | TT-DSXTA2604B | PT-DSXTA2601B
|  |  | Phase:SIP_TA28 | TT-DSXTA2801A | TT-DSXTA2801A | TT-DSXTA2805A | TT-DSXTA2804A | PT-DSXTA2801A
|  |  | Phase:SIP_TA29 | TT-DSXTA2801B | TT-DSXTA2801B | TT-DSXTA2805B | TT-DSXTA2804B | PT-DSXTA2801B
|  |  | Phase:SIP_TA31 | TT-DSXTA3101A | TT-DSXTA3101A | TT-DSXTA3105A | TT-DSXTA3104A | PT-DSXTA3101A
|  |  | Phase:SIP_TA16 | TT-DSXTA1601A | TT-DSXTA1601A | TT-DSXTA1605A | TT-DSXTA1604A | PT-DSXTA1601A
|  |  | Phase:SIP_TA18 | TT-DSXTA1601B | TT-DSXTA1601B | TT-DSXTA1605B | TT-DSXTA1604B | PT-DSXTA1601B
|  |  | Phase:SIP_TA22 | TT-DSXTA2201A | TT-DSXTA2201A | TT-DSXTA2205A | TT-DSXTA2204A | PT-DSXTA2201A
|  |  | Phase:SIP_TA24 | TT-DSXTA2201B | TT-DSXTA2201B | TT-DSXTA2205B | TT-DSXTA2204B | PT-DSXTA2201B
|  |  | Phase:SIP_TA20 | TT-DSXTA2001A | TT-DSXTA2001A | TT-DSXTA2005A | TT-DSXTA2004A | PT-DSXTA2001A
|  |  | Phase:SIP_TA17 | TT-DSXTA1701A | TT-DSXTA1701A | TT-DSXTA1705A | TT-DSXTA1704A | PT-DSXTA1701A
|  |  | Phase:SIP_TA19 | TT-DSXTA1701B | TT-DSXTA1701B | TT-DSXTA1705B | TT-DSXTA1704B | PT-DSXTA1701B
|  |  | Phase:SIP_TA21 | TT-DSXTA2101A | TT-DSXTA2101A | TT-DSXTA2105A | TT-DSXTA2104A | PT-DSXTA2101A
|  |  | Phase:SIP_TA23 | TT-DSXTA2101B | TT-DSXTA2101B | TT-DSXTA2105B | TT-DSXTA2104B | PT-DSXTA2101B
|  |  | Phase:SIP_TA30 | TT-DSXTA3001A | TT-DSXTA3001A | TT-DSXTA3005A | TT-DSXTA3004A | PT-DSXTA3001A

## SFC_HOLD_ABORT_STOP
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase(Note4) | EM
Buffer Prep Tank |  | Phase:SIP_TA12 | EM_DSXBP_CS | EM_DSXTA12_HEAD | EM_DSXTA12_TOP | EM_DSXTA12_BOM | EM_DSXBP_PS | EM_DSXTA12_JC | EM_DSXTA12_FA
|  | Phase:SIP_TA13 | EM_DSXBP_CS | EM_DSXTA13_HEAD | EM_DSXTA13_TOP | EM_DSXTA13_BOM | EM_DSXBP_PS | EM_DSXTA13_JC | EM_DSXTA13_FA
|  | Phase:SIP_TA14 | EM_DSXBP_CS | EM_DSXTA14_HEAD | EM_DSXTA14_TOP | EM_DSXTA14_BOM | EM_DSXBP_PS | EM_DSXTA14_JC | EM_DSXTA14_FA
|  | Phase:SIP_TA15 | EM_DSXBP_CS | EM_DSXTA15_HEAD | EM_DSXTA15_TOP | EM_DSXTA15_BOM | EM_DSXBP_PS | EM_DSXTA15_JC | EM_DSXTA15_FA
Buffer Hold Tank |  | Phase:SIP_TA20 | EM_DSXBH3_CS | EM_DSXTA20_HEAD | EM_DSXTA20_TOP | EM_DSXTA20_BOM | EM_DSXBH3_PS | EM_DSXTA20_JC | EM_DSXTA20_FA
|  | Phase:SIP_TA16 | EM_DSXBH3_CS | EM_DSXTA16_HEAD | EM_DSXTA16_TOP | EM_DSXTA16_BOM | EM_DSXBH3_PS | EM_DSXTA16_JC | EM_DSXTA16_FA
|  | Phase:SIP_TA17 | EM_DSXBH4_CS | EM_DSXTA17_HEAD | EM_DSXTA17_TOP | EM_DSXTA17_BOM | EM_DSXBH4_PS | EM_DSXTA17_JC | EM_DSXTA17_FA
|  | Phase:SIP_TA18 | EM_DSXBH3_CS | EM_DSXTA18_HEAD | EM_DSXTA18_TOP | EM_DSXTA18_BOM | EM_DSXBH3_PS | EM_DSXTA18_JC | EM_DSXTA18_FA
|  | Phase:SIP_TA19 | EM_DSXBH4_CS | EM_DSXTA19_HEAD | EM_DSXTA19_TOP | EM_DSXTA19_BOM | EM_DSXBH4_PS | EM_DSXTA19_JC | EM_DSXTA19_FA
|  | Phase:SIP_TA21 | EM_DSXBH4_CS | EM_DSXTA21_HEAD | EM_DSXTA21_TOP | EM_DSXTA21_BOM | EM_DSXBH4_PS | EM_DSXTA21_JC | EM_DSXTA21_FA
|  | Phase:SIP_TA22 | EM_DSXBH3_CS | EM_DSXTA22_HEAD | EM_DSXTA22_TOP | EM_DSXTA22_BOM | EM_DSXBH3_PS | EM_DSXTA22_JC | EM_DSXTA22_FA
|  | Phase:SIP_TA23 | EM_DSXBH4_CS | EM_DSXTA23_HEAD | EM_DSXTA23_TOP | EM_DSXTA23_BOM | EM_DSXBH4_PS | EM_DSXTA23_JC | EM_DSXTA23_FA
|  | Phase:SIP_TA24 | EM_DSXBH3_CS | EM_DSXTA24_HEAD | EM_DSXTA24_TOP | EM_DSXTA24_BOM | EM_DSXBH3_PS | EM_DSXTA24_JC | EM_DSXTA24_FA
|  | Phase:SIP_TA26 | EM_DSXBH2_CS | EM_DSXTA26_HEAD | EM_DSXTA26_TOP | EM_DSXTA26_BOM | EM_DSXBH2_PS | EM_DSXTA26_JC | EM_DSXTA26_FA
|  | Phase:SIP_TA27 | EM_DSXBH2_CS | EM_DSXTA27_HEAD | EM_DSXTA27_TOP | EM_DSXTA27_BOM | EM_DSXBH2_PS | EM_DSXTA27_JC | EM_DSXTA27_FA
|  | Phase:SIP_TA28 | EM_DSXBH2_CS | EM_DSXTA28_HEAD | EM_DSXTA28_TOP | EM_DSXTA28_BOM | EM_DSXBH2_PS | EM_DSXTA28_JC | EM_DSXTA28_FA
|  | Phase:SIP_TA29 | EM_DSXBH2_CS | EM_DSXTA29_HEAD | EM_DSXTA29_TOP | EM_DSXTA29_BOM | EM_DSXBH2_PS | EM_DSXTA29_JC | EM_DSXTA29_FA
|  | Phase:SIP_TA30 | EM_DSXBH4_CS | EM_DSXTA30_HEAD | EM_DSXTA30_TOP | EM_DSXTA30_BOM | EM_DSXBH4_PS | EM_DSXTA30_JC | EM_DSXTA30_FA
|  | Phase:SIP_TA31 | EM_DSXBH2_CS | EM_DSXTA31_HEAD | EM_DSXTA31_TOP | EM_DSXTA31_BOM | EM_DSXBH2_PS | EM_DSXTA31_JC | EM_DSXTA31_FA
|  | Phase:SIP_TA32 | EM_DSXBH1_CS | EM_DSXTA32_HEAD | EM_DSXTA32_TOP | EM_DSXTA32_BOM | EM_DSXBH1_PS | EM_DSXTA32_JC | EM_DSXTA32_FA
|  | Phase:SIP_TA33 | EM_DSXBH1_CS | EM_DSXTA33_HEAD | EM_DSXTA33_TOP | EM_DSXTA33_BOM | EM_DSXBH1_PS | EM_DSXTA33_JC | EM_DSXTA33_FA
|  | Phase:SIP_TA34 | EM_DSXBH1_CS | EM_DSXTA34_HEAD | EM_DSXTA34_TOP | EM_DSXTA34_BOM | EM_DSXBH1_PS | EM_DSXTA34_JC | EM_DSXTA34_FA
|  | Phase:SIP_TA35 | EM_DSXBH1_CS | EM_DSXTA35_HEAD | EM_DSXTA35_TOP | EM_DSXTA35_BOM | EM_DSXBH1_PS | EM_DSXTA35_JC | EM_DSXTA35_FA
Step |  | Description | EM_BUF_CS | EM_BP_HEAD/ EM_BH_HEAD | EM_BP_TOP/ EM_BH_TOP | EM_BP_BOM/ EM_BH_BOM | EM_BUF_PS | EM_BUF_JC | EM_BP_FA/ EM_BH_FA | Alarm Settings | Controller Settings | Other Actions | REV.2 | 删除EM
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1000 | JC_DRAIN | SIP之前夹套排空 Jacket drain before SIP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | JC_DRN | CLOSE
S1010 | JC_HEAT | 夹套通入工业蒸汽辅助加热罐体 Heat tank by industrial steam into jacket. | CLOSE | CLOSE | CLOSE | CLOSE | PS_SUPPLY | JC_HEAT | VENT_FA | Enable "HM" if TT <R_JC_HEAT_TT_SP when Step_Timer is over
S1020 | HEAT_1 | 罐体通入纯蒸汽加热，打开排放旁路，排除凝水，罐体继续升温。 Heat tank by clean steam into tank and drain condensate water by bypass valve. | CS_SUPPLY | SIP_TK | SIP_TK | SIP_TK_HEAT | PS_SUPPLY | JC_HEAT | SIP_FA | Enable"HM" if TT <R_HEAT_TT_SP when Step_Timer is over | SP: EM_BUF_CS_PIC OUT= R_CS_PT_SP1; EM_DSXBHX_CS_PIC OUT= R_CS_PT_SP1;
S1030 | HEAT_2 | 罐体通入纯蒸汽加热，只通过疏水阀排除凝水，罐体继续升温。 Heat tank by clean steam into tank and drain by steam trap valve. | CS_SUPPLY | SIP_TK | SIP_TK | SIP_TK | CLOSE | CLOSE | SIP_FA | Enable "HM" if TT <R_SIP_TT_SP when Step_Timer is over | SP: EM_BUF_CS_PIC OUT= R_CS_PT_SP2; EM_DSXBHX_CS_PIC OUT= R_CS_PT_SP2; | Release EM_BUF_PS.
S1040 | STERILIZE | 灭菌计时 Sterilize timer. | CS_SUPPLY | SIP_TK | SIP_TK | SIP_TK | N/A | CLOSE | SIP_FA
S1050 | REPLACE_AIR | 罐子空气置换 Replace the Air of Vessel | CLOSE | CLOSE | CLOSE | SIP_TK_HEAT | N/A | CLOSE | PA_TK | Enable "HM" if TT >R_COOL_TT_SP_1 when Step_Timer is over |  | Release EM_BUF_CS.
S1060 | COOL_1 | 夹套通低流量冷却介质降温罐子 Cool Vessel by Low Flow of Water | N/A | CLOSE | CLOSE | SIP_TK | N/A | JC_COOL_PUL | PRESSURE_CONT | Enable "HM" if TT >R_COOL_TT_SP_2 when Step_Timer is over | SP: EM_BP(BH)_FA_PIT01* =PT(Note3); EM_BP(BH)_FA_SP =R_PRS_PT_SP; EM_BP(BH)_FA_△P =R_PRS_PT_SP_DEV
S1070 | COOL_2 | 夹套通高流量冷却介质降温罐子 Cool Vessel by High Flow of Water | N/A | CLOSE | CLOSE | SIP_TK | N/A | JC_COOL | PRESSURE_CONT | Enable "HM" if TT >R_COOL_TT_SP_3 when Step_Timer is over | SP: EM_BP(BH)_FA_PIT01* =PT(Note3); EM_BP(BH)_FA_SP =R_PRS_PT_SP; EM_BP(BH)_FA_△P =R_PRS_PT_SP_DEV
S1080 | PRESS_HOLD | 罐体保压。 Tank keep pressure at set point. | N/A | CLOSE | CLOSE | CLOSE | N/A | CLOSE | PRESSURE_CONT |  | SP: EM_BP(BH)_FA_PIT01* =PT(Note3); EM_BP(BH)_FA_SP =R_PRS_PT_SP; EM_BP(BH)_FA_△P =R_PRS_PT_SP_DEV
S1090 | JC_DRAIN | SIP之后夹套排空 Jacket drain after SIP | N/A | CLOSE | CLOSE | CLOSE | N/A | JC_DRN | CLOSE
S1100 | CLOSE | 关闭所有阀门。 Close all valve. | N/A | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE
S1110 | SET_STATE | 状态变更 Set State | N/A | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE |  |  | Change the state to SIPed | Change the state to Aseptic.
S1200 | REHEAT | 重新加热通过加入纯蒸汽。 Reheat tank by into clean stean. | CS_SUPPLY | SIP_TK | SIP_TK | SIP_TK | N/A | CLOSE | SIP_FA |  | SP: EM_BUF_CS_PIC OUT= R_CS_PT_SP1
S7000 | HOLD | 暂停 pause | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD
S8000 | REPLACE_AIR | 罐子空气置换 Replace the Air of Vessel | CLOSE | CLOSE | CLOSE | SIP_TK_HEAT | CLOSE | CLOSE | PA_TK | Enable "HM" if TT >R_COOL_TT_SP_1 when Step_Timer is over |  | Release EM_BUF_PS and EM_BUF_CS.
S8010 | COOL_1 | 夹套通低流量冷却介质降温罐子 Cool Vessel by Low Flow of Water | N/A | CLOSE | CLOSE | SIP_TK | N/A | CLOSE | PRESSURE_CONT | Enable "HM" if TT >R_COOL_TT_SP_2 when Step_Timer is over | SP: EM_BP(BH)_FA_PIT01* =PT(Note3); EM_BP(BH)_FA_SP =R_PRS_PT_SP; EM_BP(BH)_FA_△P =R_PRS_PT_SP_DEV
S8020 | COOL_2 | 夹套通高流量冷却介质降温罐子 Cool Vessel by High Flow of Water | N/A | CLOSE | CLOSE | SIP_TK | N/A | JC_COOL | PRESSURE_CONT | Enable "HM" if TT >R_COOL_TT_SP_3 when Step_Timer is over | SP: EM_BP(BH)_FA_PIT01* =PT(Note3); EM_BP(BH)_FA_SP =R_PRS_PT_SP; EM_BP(BH)_FA_△P =R_PRS_PT_SP_DEV
S8030 | JC_DRAIN | SIP之后夹套排空 Jacket drain after SIP | N/A | CLOSE | CLOSE | CLOSE | N/A | JC_DRN | CLOSE
S8040 | CLOSE | 关闭所有阀门。 Close all valve. | N/A | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE |  |  |  |  | 删除两个TT
S8050 | SET_STATE | 状态变更 Set State | N/A | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE |  |  | Change the state to Clean.
Note4：All the phases existed in DS1/DS2/DS3/DS4.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_CS_PT_SP1 | YES | Steam pressure set point for pre-heating pipe | real | barg | 2 | 0 | 2.5
| R_CS_PT_SP2 | YES | Steam pressure set point for sterilize pipe | real | barg | 1.2 | 0 | 2.5
| R_S1000_ELAP_TM | NO | Jacket drain time | real | min | 2 | 1 | 100
| R_S1010_STEP_TM | NO | maximum jacket-heating time,hold if exceed the time | real | min | 30 | 5 | 100
| R_S1020_STEP_TM | NO | maximum pre-heating time, hold if exceed the time | real | min | 30 | 5 | 100
| R_S1030_STEP_TM | NO | maximum heating time,hold if exceed the time | real | min | 30 | 5 | 100
| R_STABLE_TM | NO | Stable time | real | min | 2 | 0 | 10
| R_SIP_TM | YES | SIP time | real | min | 30 | 0 | 60
| R_S1050_STEP_TM | NO | maximum pre-cooling time,hold if exceed the time | real | min | 60 | 1 | 100
| R_S1060_STEP_TM | NO | maximum jacket low flow cooling time,hold if exceed the time | real | min | 60 | 1 | 100
| R_S1070_STEP_TM | NO | maximum jacket high flow cooling time,hold if exceed the time | real | min | 60 | 1 | 100 | （）
| R_S1090_ELAP_TM | NO | Jacket drain time | real | min | 2 | 1 | 100
| R_JC_HEAT_TT_SP | YES | temperature set point for vessel jacket heating | real | °C | 40 | 30 | 100
| R_HEAT_TT_SP | YES | temperature set point for vessel pre-heating | real | °C | 95 | 80 | 100
| R_SIP_TT_SP | YES | SIP control temperature | real | °C | 123 | 121 | 125
| R_SIP_TT_SP_DEV | NO | SIP temperature Deviation | Real | °C | 1 | 0 | 99
| R_COOL_TT_SP_1 | YES | temperature set point for COOL_VESSEL_1 | real | °C | 105 | 0 | 110
| R_COOL_TT_SP_2 | YES | temperature set point for COOL_VESSEL_2 | real | °C | 95 | 0 | 110
| R_COOL_TT_SP_3 | YES | temperature set point for COOL_VESSEL_3 | real | °C | 60 | 0 | 110
| R_PRS_PT_SP | YES | Final pressure set point for tank pressurization | real | barg | 0.5 | 0 | 1.5
| R_PRS_PT_SP_DEV | YES | Final pressure deviation set point for tank pressurization | real | barg | 0.1 | 0 | 1.5
| R_S8030_ELAP_TM | NO | Jacket drain time | real | min | 2 | 1 | 100
11. | Report Parameter (RP) Table
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_SIP_TM |  | SIP time | real | min
| L_SIP_TT_PV |  | SIP control temperature | real | °C
| L_COOL_TT_PV_1 |  | Temperature for COOL_VESSEL_1 | real | °C
| L_COOL_TT_PV_2 |  | Temperature for COOL_VESSEL_2 | real | °C
| L_PRS_PT_PV |  | Pressure for tank Pressurization | real | barg
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXBP01/E-DSXBH01 Emergency Stop
| Hold03 |  | Step timer S1010~S1080 elapsed
| Hold04 |  | Any TT fault
13 | Indication Table
| Code |  | Description
| prompt |  | Step timer S130~170 elapsed

## ALARM (hidden)
INDICATION | S150~S180