## Cover Sheet
Phase Specification
PH_P_BP
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004186 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-04-12 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-04-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-11-06 | 杜林茂 | Draft
| 0.1a | 2020-11-20 | 杜林茂 | hold/abort 修改
| 0.1b | 2020-12-10 | 杜林茂 | 1. SFC_RUN: 增加S1071，S1072 2. Action Table: 增加参数报警 3. ParameterHold Tables： 删除Hold06; 增加CT和pH报警参数
| 1.0 | 2021-03-03 | 杜林茂 | 1. SFC_RUN: 更新配液逻辑 2. Action Table：根据顺控图对应更新 3. ParameterHold Tables：更新INPUT和REPORT参数 4. 根据FAT修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号

## Description
6. | Description
The Phase TK_WFI_IN is used for adding WFI into tank or WFI point sample. 1. DCS will control the POU valve which supplied and installed by CU system.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Buffer Preparation Tank | 3000L BUFFER PREPARATION TANK UNIT TA12 | DS1-TA12
|  | 3000L BUFFER PREPARATION TANK UNIT TA13 | DS1-TA13
|  | 6000L BUFFER PREPARATION TANK UNIT TA14 | DS1-TA14
|  | 9000L BUFFER PREPARATION TANK UNIT TA15 | DS1-TA15
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Buffer Preparation Tank | EM_BP_TOP
AG01
EM_BP_FA
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| N/A | N/A

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
|  | Phase | Note1
|  | PH_P_DSXTA12 | WIT-DSXTA1301C
|  | PH_P_DSXTA13 | WIT-DSXTA1301B
|  | PH_P_DSXTA14 | WIT-DSXTA1501C
|  | PH_P_DSXTA15 | WIT-DSXTA1501B
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase | EM
Buffer Prepration Tank |  | PH_P_DSXTA12 | EM_DSXTA12_TOP | EM_DSXTA12_FA | AG_DSXTA1201
|  | PH_P_DSXTA13 | EM_DSXTA13_TOP | EM_DSXTA13_FA | AG_DSXTA1301
|  | PH_P_DSXTA14 | EM_DSXTA14_TOP | EM_DSXTA14_FA | AG_DSXTA1401
|  | PH_P_DSXTA15 | EM_DSXTA15_TOP | EM_DSXTA15_FA | AG_DSXTA1501
Step |  | Description | EM_BP_TOP | EM_BP_FA | AG01 | Alarm Settings | Controller Settings | Other Actions | REV.2 | 删除EM
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A
S1010 | TARE_ BALANCE | 平衡称重 Tare the balance | CLOSE | VENT_FA | STOP
S1011 | MESSAGE | 提示是否继续 Prompt to continue | CLOSE | VENT_FA | STOP
S1020 | WFI_FEEDING1 | 高流量WFI加注 WFI feeding with high flow | WFI_SPRAY | VENT_FA | STOP | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP1 |  | Record WIT01
S1030 | MESSAGE | 提示记录加水重量 Prompt to check weight of WFI adding | CLOSE | VENT_FA | STOP
S1040 | AGITATION1 | 运行搅拌 Run the agitator | CLOSE | VENT_FA | START |  |  | AG01 Speed= R_SPD_AG_MATER
S1050 | ADD_MATERIAL | 提示添加物料 Prompt to add raw material | CLOSE | VENT_FA | START |  |  | Record material name as MATRIAL01
S1070 | PH_ADJUST | 手动调PH Adjust PH manually | CLOSE | VENT_FA | START
S1100 | STOP_AG | 停止搅拌 Stop the agitator | CLOSE | VENT_FA | STOP
S1110 | WFI_FEEDING2 | 高流量WFI加注 WFI feeding with high flow | WFI_SPRAY | VENT_FA | STOP | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP2
S1120 | WFI_FILLING | 低流量WFI加注 WFI feeding with low flow | WFI_IN | VENT_FA | STOP | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP3
S1130 | AGITATION2 | 运行搅拌 Run the agitator | CLOSE | VENT_FA | START |  |  | AG01 Speed= R_SPD_AG_BUF
S1140 | MESSAGE | 提示检查pH和CT Prompt to check pH and CT | CLOSE | VENT_FA | START
S1170 | STOP_AG | 停止搅拌 Stop the agitator | CLOSE | VENT_FA | STOP
S1180 | MESSAGE | 提示取样并记录最终配液重量 Prompt to sample and check weight of final buffer | CLOSE | VENT_FA | STOP
S1190 | PRES_CONTROL | 保压 Pressure control | CLOSE | PRESSURE_CONT | STOP |  | EM_BP_FA: SP=R_BP_PT_SP △P=R_BP_PT_SP_DEV | Record WIT01
S1200 | SET_STATE | 设置状态 Set the state | CLOSE | PRESSURE_CONT | STOP |  |  | Set State as 'Process'
S7010 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD
S8010 | ABORT | 终止 Abort | CLOSE | CLOSE | STOP
S8020 | SET_STATE | 设置状态 Set the state | CLOSE | CLOSE | STOP |  |  | Set State as 'SIPed'

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_BP_WT_BALANCE | YES | Weight setpoint for BP tank balance | real | kg | 0 | 0 | 10000
| R_Level_AG_RUN | YES | Level for agitator running | real | kg | 500 | 0 | 10000
| R_BP_WT_WFI1_SP | YES | Weight setpoint after first batch WFI adding | real | kg | 6300 | 0 | 10000
| R_BP_WT_WFI2_SP | YES | Weight setpoint after second batch WFI adding | real | kg | 8100 | 0 | 10000
| R_BP_WT_WFI3_SP | YES | Weight setpoint after final batch WFI adding | real | kg | 9000 | 0 | 10000
| R_BP_WT_BUF_SP | YES | Weight setpoint after material adding | real | kg | 9000 | 0 | 10000
| R_BP_PT_SP | YES | BP tank pressure control setpoint | real | barg | 0.5 | 0 | 3
| R_BP_PT_SP_DEV | NO | BP tank pressure control setpoint deviation | real | barg | 0.1 | 0 | 1
| MATERIAL01 | YES | Meterial name 01 | N/A | N/A | N/A | N/A | N/A
| R_SPD_AG_MATER | YES | Speed of agitator of mixing meterial with first batch WFI | int | rpm | 100 | 0 | 380
| R_SPD_AG_BUF | YES | Speed of agitator of mixing final buffer preparaed | int | rpm | 100 | 0 | 380
| R_TM_AG_MATER | YES | Time of mixing final buffer preparaed | real | min | 10 | 0 | 100
| R_TM_AG | YES | Time of mixing final buffer preparaed | real | min | 10 | 0 | 100
| R_MAX_TM_STEP1 | NO | Step Maximum Execution Time for first batch WFI adding | real | min | 10 | 1 | 3000
| R_MAX_TM_STEP2 | NO | Step Maximum Execution Time for second batch WFI adding | real | min | 10 | 1 | 3000
| R_MAX_TM_STEP3 | NO | Step Maximum Execution Time for third batch WFI adding | real | min | 10 | 1 | 3000
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng. Unit | Step | Begin | End
| L_MATERIAL01 |  | The name of material being added | N/A | N/A | 1030 | N/A | N/A
| L_BP_WT_WFI1_PV |  | Weight of first batch WFI adding | real | kg | 1120
| L_BP_WT_BUF_PV |  | Fianl weight of buffer preparation | real | kg | 1160
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXBP01 Emergency Stop
| Hold03 |  | WIT fault
| Hold04 |  | AG01 fault
| Hold05 |  | R_MAX_TM_STEP elapsed

## ALARM (hidden)
INDICATION | S150~S180