## Cover Sheet
Phase Specification
PH_TA20_WFI_IN
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004271 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-04-12 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-04-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-11-06 | 杜林茂 | Draft
0.1
0.2
0.3
| 0.1a | 2020-11-20 | 杜林茂 | hold abort命令更新
| 1.0 | 2021-03-03 | 杜林茂 | 1.SFC_RUN: 增加自动补水，自动排放和加水温度判断逻辑； 增加非自结束选项 2. Action Table：根据顺控图更新 3. ParameterHold Tables：更新INPUT和REPORT参数 4. 根据FAT修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号

## Description
6. | Description
The Phase TA20_WFI_IN is used for adding WFI into tank. 1. DCS will control the POU valve which supplied and installed by CU system.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Buffer Holding Tank | 3000L PROCESS WATER TANK UNIT TA20 | DS1-TA12
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Buffer Holiding Tank | EM_BH_TOP
| Buffer Holiding Tank | EM_BH_FA
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| N/A | N/A

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
Phase
DSXTA20_WFI_IN
Note1
LIT-DSXTA2001
Note 2
PIT-DSXTA2001
Note 3
TIT-DSXTA2001
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase | EM
Buffer Holding Tank |  | DSXTA20_PW_BH | EM_DSXTA20_TOP | EM_DSXTA20_FA | EM_DSXTA20_BOM
Step |  | Description | EM_BP_TOP | EM_BH_FA | EM_BH_BOM | Alarm Settings | Controller Settings | Other Actions | REV.2 | 删除EM
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A
S1009 | CHECK_TEMP | 罐体温度判断 Tank temperature check | CLOSE | CLOSE | CLOSE
S1010 | PRES_CONTROL | 保压 Pressure control | CLOSE | PRESSURE_CONT | N/A |  | EM_BH_FA: SP=R_BH_PI_SP SP_L=R_BH_PI_SP-R_△BH_P SP_H=R_BH_PI_SP+R_△BH_P
S1020 | LEVEL_CONTROL | WFI液位控制 WFI level control | LEVEL CONTROL | PRESSURE_CONT | N/A | Enable HM&SM R_TM_WFI_VAL | EM_BP_TOP: SP=R_LI_HIGH_SP SP_L=R_LI_LOW_SP | Start R_TM_WFI_VAL at start of S1020
S1030 | MESSAGE | 提示是否排空罐 Prompt to drain the tank | CLOSE | VENT_FA | N/A | Enable HM&SM R_TM_WAITING |  | Start R_TM_WAITING at start of S1030
S1040 | DRAIN | 排空罐 Drain the tank | CLOSE | VENT_FA | TK_DRN
S2010 | DEACTIVE | 结束 Deactive | CLOSE | CLOSE | CLOSE
S7010 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD
S8010 | ABORT | 终止 Abort | ABORT | ABORT | ABORT
S8020 | SET_STATE | 设置状态 Set the state | CLOSE | CLOSE | CLOSE |  |  | Target Tank = SIPed Line State = SIPed

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_BH_LT_SP | YES | Level setpoint for BH tank balance | real | L | 0 | 0 | 10000
| R_LI_HIGH_SP | YES | Required level setpoint of WFI adding | real | L | 2500 | 0 | 10000
| R_LI_LOW_SP | YES | Low level setpoint of WFI in tank | real | L | 100 | 0 | 10000
| R_TI_HIGH_SP | YES | High temperature setpoint of WFI tank | real | °C |  | 0 | 30
| R_BH_PI_SP | YES | BH tank pressure control setpoint | real | barg | 0.5 | 0 | 3
| R_BH_PI_SP_DEV | NO | Deviation | real | barg | 0.1 | 0 | 1
| R_TM_WFI_VAL | YES | Period of validility for WFI in the tank | real | h | 48 | 24 | 3000
| R_TM_WAITING | YES | Time for operator to confirm draining WFI tank | real | h | 120 | 1 | 3000
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng. Unit | Step | Begin | End
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXBH01 Emergency Stop
| Hold03 |  | LIT fault
| Hold04 |  | R_MAX_TM_STEP elapsed
| Hold05 |  | Clean Utility fault
| Hold06 |  | R_TM_WFI_VAL elapsed

## ALARM (hidden)
INDICATION | S150~S180