## Cover Sheet
Phase Specification
PH_VAL_CWFI_BUF
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  |  | Document No. |  | Revision
M2 Project |  |  |  | PP20-0098-T-004189 |  | 3.0
|  | Initials | Date |  | Signature
Morimatsu prepared: |  | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: |  | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:
E-DSXBP01/E-DSXCIP02 Emergency Stop is Only for Buffer Prep Tank Uint Class E-DSXBH01/E-DSXCIP02 Emergency Stop is Only for Buffer Holding Tank Uint Class

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-11-06 | 杜林茂 | Draft
0.1
0.2
0.3
| 0.1a | 2020-11-20 | 杜林茂 | hold/abort 更新
| 0.1b | 2020-12-10 | 杜林茂 | Action Table: S1030~1050 EM_BH_TOP对应command改为CIP_TK
| 1.0 | 2021-03-03 | 杜林茂 | 1.SFC_RUN：更新S1050结束判断条件 2.Action Table： 删除Note5&8&9，更新Note4； 更新S1040，S1050对应command； 3.ParameterHold Tables：更新INPUT参数，增加排放压力参数
| 2.0 | 2021-04-26 | 王树深 | 增加急停编号
| 2.0b | 2021-06-05 | 王树深 | 更新急停策略
| 2.0c | 2021-06-25 | 王树深 | 更新急停策略
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase VAL_CWFI_BUF is used for validation of CWFI into tank. 1. DCS will control the POU valve which supplied and installed by CU system.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Buffer Preparation Tank | 3000L BUFFER PREPARATION TANK UNIT TA12
3000L BUFFER PREPARATION TANK UNIT TA13
6000L BUFFER PREPARATION TANK UNIT TA14
9000L BUFFER PREPARATION TANK UNIT TA15
| Buffer Holding Tank | 3000L BUFFER HOLDING TANK UNIT TA16
3000L BUFFER HOLDING TANK UNIT TA17
3000L BUFFER HOLDING TANK UNIT TA18
3000L BUFFER HOLDING TANK UNIT TA19
3000L PROCESS WATER TANK UNIT TA20
3000L BUFFER HOLDING TANK UNIT TA21
3000L BUFFER HOLDING TANK UNIT TA22
3000L BUFFER HOLDING TANK UNIT TA23
3000L BUFFER HOLDING TANK UNIT TA24
6000L 0.1M NaOH TANK UNIT TA26
6000L BUFFER HOLDING TANK UNIT TA27
6000L BUFFER HOLDING TANK UNIT TA28
6000L BUFFER HOLDING TANK UNIT TA29
3000L BUFFER HOLDING TANK UNIT TA30
6000L BUFFER HOLDING TANK UNIT TA31
9000L 0.5M NaOH TANK UNIT TA32
9000L BUFFER HOLDING TANK UNIT TA33
9000L BUFFER HOLDING TANK UNIT TA34
9000L BUFFER HOLDING TANK UNIT TA35
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Buffer Preparation Tank | EM_BP_HEAD
EM_BP_TOP
EM_BP_FA
EM_BP_BOM
EM_BCIP_CIPS
EM_BUF_CIPS
| Buffer Holiding Tank | EM_BH_HEAD
EM_BH_TOP
EM_BH_FA
EM_BH_BOM
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| CIP Station | EM_C_CIP
EM_C_SUP
EM_C_BTH

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | RUN Logic with Check Steps
E-DSXBP01/E-DSXCIP02 Emergency Stop is Only for Buffer Prep Tank Uint Class E-DSXBH01/E-DSXCIP02 Emergency Stop is Only for Buffer Holding Tank Uint Class
| Note1: | R_SELECT_STATION is 03 or 05. Default of R_SELECT_STATION can be modified.
If R_SELECT_STATION is 03, select CIP03 if CIP03 is standby. Select CIP05 if CIP03 is occupied.

## SFC_RUN
8. | RUN Logic with Check Steps
|  | Phase (Note2) | Note1 | Note2
|  | VAL_CWFI_DXSTA12 | WIT-DSXTA1301C | N/A
|  | VAL_CWFI_DXSTA13 | WIT-DSXTA1301B | N/A
|  | VAL_CWFI_DXSTA14 | WIT-DSXTA1501C | N/A
|  | VAL_CWFI_DXSTA15 | WIT-DSXTA1501B | N/A
|  | VAL_CWFI_DXSTA16 | N/A | LIT-DSXTA1601A
|  | VAL_CWFI_DXSTA17 | N/A | LIT-DSXTA1701A
|  | VAL_CWFI_DXSTA18 | N/A | LIT-DSXTA1601B
|  | VAL_CWFI_DXSTA19 | N/A | LIT-DSXTA1701B
|  | VAL_CWFI_DXSTA20 | N/A | LIT-DSXTA2001A
|  | VAL_CWFI_DXSTA21 | N/A | LIT-DSXTA2101A
|  | VAL_CWFI_DXSTA22 | N/A | LIT-DSXTA2201A
|  | VAL_CWFI_DXSTA23 | N/A | LIT-DSXTA2101B
|  | VAL_CWFI_DXSTA24 | N/A | LIT-DSXTA2201B
|  | VAL_CWFI_DXSTA26 | N/A | LIT-DSXTA2601A
|  | VAL_CWFI_DXSTA27 | N/A | LIT-DSXTA2601B
|  | VAL_CWFI_DXSTA28 | N/A | LIT-DSXTA2801A
|  | VAL_CWFI_DXSTA29 | N/A | LIT-DSXTA2801B
|  | VAL_CWFI_DXSTA30 | N/A | LIT-DSXTA3001A
|  | VAL_CWFI_DXSTA31 | N/A | LIT-DSXTA3101A
|  | VAL_CWFI_DXSTA32 | N/A | LIT-DSXTA3201A
|  | VAL_CWFI_DXSTA33 | N/A | LIT-DSXTA3201B
|  | VAL_CWFI_DXSTA34 | N/A | LIT-DSXTA3401A
|  | VAL_CWFI_DXSTA35 | N/A | LIT-DSXTA3401B
Note2: | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.
E-DSXBP01/E-DSXCIP02 Emergency Stop is Only for Buffer Prep Tank Uint Class E-DSXBH01/E-DSXCIP02 Emergency Stop is Only for Buffer Holding Tank Uint Class

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
| Unit Class | Phase
| Buffer Preparation System | VAL_CWFI_DXSTA12 | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note4) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | EM_DSXBP_CIPS | EM_DSXTA12_HEAD | N/A | EM_DSXTA12_TOP | N/A | EM_DSXTA12_FA | N/A | EM_DSXTA12_BOM | N/A
|  | VAL_CWFI_DXSTA13 | [5 empty] | EM_DSXTA13_HEAD | N/A | EM_DSXTA13_TOP | N/A | EM_DSXTA13_FA | N/A | EM_DSXTA13_BOM | N/A
|  | VAL_CWFI_DXSTA14 | [5 empty] | EM_DSXTA14_HEAD | N/A | EM_DSXTA14_TOP | N/A | EM_DSXTA14_FA | N/A | EM_DSXTA14_BOM | N/A
|  | VAL_CWFI_DXSTA15 | [5 empty] | EM_DSXTA15_HEAD | N/A | EM_DSXTA15_TOP | N/A | EM_DSXTA15_FA | N/A | EM_DSXTA15_BOM | N/A
| Buffer Holding System | VAL_CWFI_DXSTA32 |  |  |  |  | EM_DSXBH1_CIPS | N/A | EM_DSXTA32_HEAD | N/A | EM_DSXTA32_TOP | N/A | EM_DSXTA32_FA | N/A | EM_DSXTA32_BOM
|  | VAL_CWFI_DXSTA33 | [5 empty] | N/A | EM_DSXTA33_HEAD | N/A | EM_DSXTA33_TOP | N/A | EM_DSXTA33_FA | N/A | EM_DSXTA33_BOM
|  | VAL_CWFI_DXSTA34 | [5 empty] | N/A | EM_DSXTA34_HEAD | N/A | EM_DSXTA34_TOP | N/A | EM_DSXTA34_FA | N/A | EM_DSXTA34_BOM
|  | VAL_CWFI_DXSTA35 | [5 empty] | N/A | EM_DSXTA35_HEAD | N/A | EM_DSXTA35_TOP | N/A | EM_DSXTA35_FA | N/A | EM_DSXTA35_BOM
|  | VAL_CWFI_DXSTA26 |  |  |  |  | EM_DSXBH2_CIPS | N/A | EM_DSXTA26_HEAD | N/A | EM_DSXTA26_TOP | N/A | EM_DSXTA26_FA | N/A | EM_DSXTA26_BOM
|  | VAL_CWFI_DXSTA27 | [5 empty] | N/A | EM_DSXTA27_HEAD | N/A | EM_DSXTA27_TOP | N/A | EM_DSXTA27_FA | N/A | EM_DSXTA27_BOM
|  | VAL_CWFI_DXSTA28 | [5 empty] | N/A | EM_DSXTA28_HEAD | N/A | EM_DSXTA28_TOP | N/A | EM_DSXTA28_FA | N/A | EM_DSXTA28_BOM
|  | VAL_CWFI_DXSTA29 | [5 empty] | N/A | EM_DSXTA29_HEAD | N/A | EM_DSXTA29_TOP | N/A | EM_DSXTA29_FA | N/A | EM_DSXTA29_BOM
|  | VAL_CWFI_DXSTA31 | [5 empty] | N/A | EM_DSXTA31_HEAD | N/A | EM_DSXTA31_TOP | N/A | EM_DSXTA31_FA | N/A | EM_DSXTA31_BOM
|  | VAL_CWFI_DXSTA16 |  |  |  |  | EM_DSXBH3_CIPS | N/A | EM_DSXTA16_HEAD | N/A | EM_DSXTA16_TOP | N/A | EM_DSXTA16_FA | N/A | EM_DSXTA16_BOM
|  | VAL_CWFI_DXSTA18 | [5 empty] | N/A | EM_DSXTA18_HEAD | N/A | EM_DSXTA18_TOP | N/A | EM_DSXTA18_FA | N/A | EM_DSXTA18_BOM
|  | VAL_CWFI_DXSTA22 | [5 empty] | N/A | EM_DSXTA22_HEAD | N/A | EM_DSXTA22_TOP | N/A | EM_DSXTA22_FA | N/A | EM_DSXTA22_BOM
|  | VAL_CWFI_DXSTA24 | [5 empty] | N/A | EM_DSXTA24_HEAD | N/A | EM_DSXTA24_TOP | N/A | EM_DSXTA24_FA | N/A | EM_DSXTA24_BOM
|  | VAL_CWFI_DXSTA20 | [5 empty] | N/A | EM_DSXTA20_HEAD | N/A | EM_DSXTA20_TOP | N/A | EM_DSXTA20_FA | N/A | EM_DSXTA20_BOM
|  | VAL_CWFI_DXSTA17 |  |  |  |  | EM_DSXBH4_CIPS | N/A | EM_DSXTA17_HEAD | N/A | EM_DSXTA17_TOP | N/A | EM_DSXTA17_FA | N/A | EM_DSXTA17_BOM
|  | VAL_CWFI_DXSTA19 | [5 empty] | N/A | EM_DSXTA19_HEAD | N/A | EM_DSXTA19_TOP | N/A | EM_DSXTA19_FA | N/A | EM_DSXTA19_BOM
|  | VAL_CWFI_DXSTA21 | [5 empty] | N/A | EM_DSXTA21_HEAD | N/A | EM_DSXTA21_TOP | N/A | EM_DSXTA21_FA | N/A | EM_DSXTA21_BOM
|  | VAL_CWFI_DXSTA23 | [5 empty] | N/A | EM_DSXTA23_HEAD | N/A | EM_DSXTA23_TOP | N/A | EM_DSXTA23_FA | N/A | EM_DSXTA23_BOM
|  | VAL_CWFI_DXSTA30 | [5 empty] | N/A | EM_DSXTA30_HEAD | N/A | EM_DSXTA30_TOP | N/A | EM_DSXTA30_FA | N/A | EM_DSXTA30_BOM
Step |  | Description | EM_C_CIP | EM_C_SUP | EM_C_BTH | EM_BCIP_CIPS | EM_BUF_CIPS | EM_BP_HEAD | EM_BH_HEAD | EM_BP_TOP | EM_BH_TOP | EM_BP_FA | EM_BH_FA | EM_BP_BOM | EM_BH_BOM | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | CHECK_MEDIUM | 检查介质 Check medium | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1020 | PREP_MEDIUM | 准备介质 CIP station medium preparation | PREP_CWFI | STOP | WT_FILTER_OPEN | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP2
S1030 | FILLING | 注水 Fill the tank with CWFI | SUPPLY_CWFI | MEDIUM_SUPPLY | WT_FILTER_OPEN | Note6 | Note7 | CIP_TK | CIP_TK | CIP_IN | CIP_TK | VENT_FA | VENT_FA | CLOSE | CLOSE
S1040 | CWFI_SAMPLE | CWFI取样 CWFI sample | STOP_PUMP | MEDIUM_SUPPLY | WT_FILTER_OPEN | Note6 | Note7 | CIP_TK | CIP_TK | CIP_IN | CIP_TK | VENT_FA | VENT_FA | CLOSE | CLOSE |  |  | Operator sample CWFI in tank
S1050 | DRAIN | 罐内水排放 Drain the tank | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | PRESSURE_CONT | PRESSURE_CONT | TK_DRN | TK_DRN |  | EM_BP_FA/EM_BH_FA: SP=R_PT_SP △P=R_PT_SP_DEV
S1060 | CLOSE | 关闭所有设备 Close all device | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S7010 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD |  |  | First close EM_C_CIP then close other EM
S8010 | ABORT | 中止步骤 Abort | STOP | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | First close EM_C_CIP then close other EM
Note1: If select CIP03 station, EM will be EM_DSXCIP03. If select CIP05 station, EM will be EM_DSXCIP05. | [5 empty] | Unit Class | Phase | Note6 | Note7
Note2: If select CIP03 station, EM will be EM_DSXCIP03_SUP. If select CIP05 station, EM will be EM_DSXCIP05_SUP. | [5 empty] | Buffer Preparation System | VAL_CWFI_DXSTA12 | CIP_TO_TA15 | CIP_TO_TA12
Note3: If select CIP03 station, EM will be EM_DSXCIP03_CIPS. If select CIP05 station, EM will be EM_DSXCIP05_CIPS. | [6 empty] | VAL_CWFI_DXSTA13 |  | CIP_TO_TA13
Note4: If select CIP03 station, EM will be EM_DSXCIP03_BTH. If select CIP05 station, EM will be EM_DSXCIP05_BTH. | [6 empty] | VAL_CWFI_DXSTA14 |  | CIP_TO_TA14
[7 empty] | VAL_CWFI_DXSTA15 |  | N/A
[6 empty] | Buffer Holding System | VAL_CWFI_DXSTA32 | CIP_TO_TA35 | CIP_TO_TA32
[7 empty] | VAL_CWFI_DXSTA33 |  | CIP_TO_TA33
[7 empty] | VAL_CWFI_DXSTA34 |  | CIP_TO_TA34
[7 empty] | VAL_CWFI_DXSTA35 |  | N/A
[7 empty] | VAL_CWFI_DXSTA26 | CIP_TO_TA31 | CIP_TO_TA26
[7 empty] | VAL_CWFI_DXSTA27 |  | CIP_TO_TA27
[7 empty] | VAL_CWFI_DXSTA28 |  | CIP_TO_TA28
[7 empty] | VAL_CWFI_DXSTA29 |  | CIP_TO_TA29
[7 empty] | VAL_CWFI_DXSTA31 |  | N/A
[7 empty] | VAL_CWFI_DXSTA16 | CIP_TO_TA16 | N/A
[7 empty] | VAL_CWFI_DXSTA18 |  | CIP_TO_TA18
[7 empty] | VAL_CWFI_DXSTA22 |  | CIP_TO_TA22
[7 empty] | VAL_CWFI_DXSTA24 |  | CIP_TO_TA24
[7 empty] | VAL_CWFI_DXSTA20 |  | CIP_TO_TA20
[7 empty] | VAL_CWFI_DXSTA17 | CIP_TO_TA17 | N/A
[7 empty] | VAL_CWFI_DXSTA19 |  | CIP_TO_TA19
[7 empty] | VAL_CWFI_DXSTA21 |  | CIP_TO_TA21
[7 empty] | VAL_CWFI_DXSTA23 |  | CIP_TO_TA23
[7 empty] | VAL_CWFI_DXSTA30 |  | CIP_TO_TA30

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_BP_WT_SP | YES | Weight setpoint of BP tank CWFI filling | real | kg | 1000 | 0 | 10000
| R_BH_LT_SP | YES | Level setpoint of BH tank CWFI filling | real | L | 1000 | 0 | 10000
| R_MAX_TM_STEP | NO | Maximum step execution time, hold if exceed the time | real | min | 150 | 0 | 360
| R_TM_CWFI_DRN | YES | Drain time for CWFI in tank and pipe | real | min | 10 | 1 | 10
| R_WT_DR_SP | YES | Weight setpoint of BP tank Drain | real | kg | 10 | 0 | 1000
| R_LT_DR_SP | YES | Level setpoint of BH tank Drain | real | L | 10 | 0 | 1000
| R_PT_SP | YES | Pressure setpoint for Tank Drain | real | bar | 0.5 | 0 | 3
| R_PT_SP_DEV | YES | Deviation | real | bar | 0.1 | 0 | 1
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description |  | Eng. Unit | Step | Begin | End
| N/A |  | N/A |  | N/A | N/A | N/A | N/A
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXBP01 Emergency Stop is Only for Buffer Preparation Tank Uint Class
| Hold03 |  | E-DSXBH01 Emergency Stop is Only for Buffer Holding Tank Uint Class
| Hold04 |  | LIT fault
| Hold05 |  | R_MAX_TM_STEP elapsed
| Hold06 |  | CIP station Hold

## ALARM (hidden)
INDICATION | S150~S180