## Cover Sheet
Phase Specification
PH_D_BUF
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004231 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, - for delimiter, EM-..... |  |  | PH-U-S-TANK
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-31 | 王树深
| 0.1a | 2020-12-10 | 王树深 | 1.SFC_RUN中判断条件修改。 2.Action Table个别commend修改。 3.ParameterHold Tables中增加参数R_S1020_STEP_TM和R_PT_DP_SP_DEV。
| 1.0 | 2021-03-03 | 王树深 | 程序仿真修改
| 2.0 | 2021-04-26 | 王树深 | 增加急停编号
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase PH_D_BUF is used for draining buffer into waste . 1. Drain into waste 2. Draining by slight overpressure
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Buffer Prep Tank | DSXTA12
DSXTA13
DSXTA14
DSXTA15
| Buffer Hold Tank | DSXTA20
DSXTA16
DSXTA17
DSXTA18
DSXTA19
DSXTA21
DSXTA22
DSXTA23
DSXTA24
DSXTA26
DSXTA27
DSXTA28
DSXTA29
DSXTA30
DSXTA31
DSXTA32
DSXTA33
DSXTA34
DSXTA35
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Buffer Prep Tank | EM_BP_FA
EM_BP_BOM
| Buffer Hold Tank | EM_BH_FA
EM_BH_BOM
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| NA | NA

## SFC_CHECK
8. | Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
|  | Unit class | Phase | PIT(Note1): | WT(Note2): | LT(Note3):
|  | Buffer Prep Tank | DRAIN_DSXTA12 | PIT-DSXTA1301B | WIT-DSXTA1201B | N/A
|  |  | DRAIN_DSXTA13 | PIT-DSXTA1301C | WIT-DSXTA1201C | N/A
|  |  | DRAIN_DSXTA14 | PIT-DSXTA1501B | WIT-DSXTA1501B | N/A
|  |  | DRAIN_DSXTA15 | PIT-DSXTA1501C | WIT-DSXTA1501C | N/A
|  | Buffer Hold Tank | DRAIN_DSXTA32 | PIT-DSXTA3201A | N/A | LIT-DSXTA3201A
|  |  | DRAIN_DSXTA33 | PIT-DSXTA3201B | N/A | LIT-DSXTA3201B
|  |  | DRAIN_DSXTA34 | PIT-DSXTA3401A | N/A | LIT-DSXTA3401A
|  |  | DRAIN_DSXTA35 | PIT-DSXTA3401B | N/A | LIT-DSXTA3401B
|  |  | DRAIN_DSXTA26 | PIT-DSXTA2601A | N/A | LIT-DSXTA2601A
|  |  | DRAIN_DSXTA27 | PIT-DSXTA2601B | N/A | LIT-DSXTA2601B
|  |  | DRAIN_DSXTA28 | PIT-DSXTA2801A | N/A | LIT-DSXTA2801A
|  |  | DRAIN_DSXTA29 | PIT-DSXTA2801B | N/A | LIT-DSXTA2801B
|  |  | DRAIN_DSXTA31 | PIT-DSXTA3101A | N/A | LIT-DSXTA3101A
|  |  | DRAIN_DSXTA16 | PIT-DSXTA1601A | N/A | LIT-DSXTA1601A
|  |  | DRAIN_DSXTA18 | PIT-DSXTA1601B | N/A | LIT-DSXTA1601B
|  |  | DRAIN_DSXTA22 | PIT-DSXTA2201A | N/A | LIT-DSXTA2201A
|  |  | DRAIN_DSXTA24 | PIT-DSXTA2201B | N/A | LIT-DSXTA2201B
|  |  | DRAIN_DSXTA20 | PIT-DSXTA2001A | N/A | LIT-DSXTA2001A
|  |  | DRAIN_DSXTA17 | PIT-DSXTA1701A | N/A | LIT-DSXTA1701A
|  |  | DRAIN_DSXTA19 | PIT-DSXTA1701B | N/A | LIT-DSXTA1701B
|  |  | DRAIN_DSXTA21 | PIT-DSXTA2101A | N/A | LIT-DSXTA2101A
|  |  | DRAIN_DSXTA23 | PIT-DSXTA2101B | N/A | LIT-DSXTA2101B
|  |  | DRAIN_DSXTA30 | PIT-DSXTA3001A | N/A | LIT-DSXTA3001A

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase
BUFFER PREPARATION |  | DRAIN_DSXTA12 | EM_DSXTA12_FA | N/A | EM_DSXTA12_BOM | N/A
|  | DRAIN_DSXTA13 | EM_DSXTA13_FA | N/A | EM_DSXTA13_BOM | N/A
|  | DRAIN_DSXTA14 | EM_DSXTA14_FA | N/A | EM_DSXTA14_BOM | N/A
|  | DRAIN_DSXTA15 | EM_DSXTA15_FA | N/A | EM_DSXTA15_BOM | N/A
BUFFER HOLDING |  | DRAIN_DSXTA16 | N/A | EM_DSXTA16_FA | N/A | EM_DSXTA16_FA
|  | DRAIN_DSXTA18 | N/A | EM_DSXTA18_FA | N/A | EM_DSXTA18_FA
|  | DRAIN_DSXTA22 | N/A | EM_DSXTA22_FA | N/A | EM_DSXTA22_FA
|  | DRAIN_DSXTA24 | N/A | EM_DSXTA24_FA | N/A | EM_DSXTA24_FA
|  | DRAIN_DSXTA20 | N/A | EM_DSXTA20_FA | N/A | EM_DSXTA20_FA
|  | DRAIN_DSXTA17 | N/A | EM_DSXTA17_FA | N/A | EM_DSXTA17_FA
|  | DRAIN_DSXTA19 | N/A | EM_DSXTA19_FA | N/A | EM_DSXTA19_FA
|  | DRAIN_DSXTA21 | N/A | EM_DSXTA21_FA | N/A | EM_DSXTA21_FA
|  | DRAIN_DSXTA23 | N/A | EM_DSXTA23_FA | N/A | EM_DSXTA23_FA
|  | DRAIN_DSXTA30 | N/A | EM_DSXTA30_FA | N/A | EM_DSXTA30_FA
|  | DRAIN_DSXTA26 | N/A | EM_DSXTA26_FA | N/A | EM_DSXTA26_FA
|  | DRAIN_DSXTA27 | N/A | EM_DSXTA27_FA | N/A | EM_DSXTA27_FA
|  | DRAIN_DSXTA28 | N/A | EM_DSXTA28_FA | N/A | EM_DSXTA28_FA
|  | DRAIN_DSXTA29 | N/A | EM_DSXTA29_FA | N/A | EM_DSXTA29_FA
|  | DRAIN_DSXTA31 | N/A | EM_DSXTA31_FA | N/A | EM_DSXTA31_FA
|  | DRAIN_DSXTA32 | N/A | EM_DSXTA32_FA | N/A | EM_DSXTA32_FA
|  | DRAIN_DSXTA33 | N/A | EM_DSXTA33_FA | N/A | EM_DSXTA33_FA
|  | DRAIN_DSXTA34 | N/A | EM_DSXTA34_FA | N/A | EM_DSXTA34_FA
|  | DRAIN_DSXTA35 | N/A | EM_DSXTA35_FA | N/A | EM_DSXTA35_FA
Step |  | Description | EM_BP_FA | EM_BH_FA | EM_BP_BOM | EM_BH_BOM | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A
S1010 | PRESS_CTRL | 通过压空加压。 Set pressure to tank and product pipe by PA. | PRESSURE_CONT | PRESSURE_CONT | CLOSE | CLOSE
S1020 | DRAIN | 打开物料管道排放 Drain of tank and product pipe | PRESSURE_CONT | PRESSURE_CONT | TK_DRN | TK_DRN | Enable "Step time alarm" if WT(Note2)>R_WT_SP or LT(Note3)>R_LT_SP when Step_Timer is over
S1030 | RELEASE PRESS | 压力泄放 Pressure relief | VENT_FA | VENT_FA | TK_DRN | TK_DRN
S1040 | CLOSE | 关闭阀门 Close the valves | CLOSE | CLOSE | CLOSE | CLOSE
S1050 | SET STATE | 设置状态 Set state | CLOSE | CLOSE | CLOSE | CLOSE
S7000 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD | HOLD
S8000 | VENT | 压力泄放 Pressure relief | VENT_FA | VENT_FA | TK_DRN | TK_DRN
S8100 | CLOSE | 关闭阀门 Close the valves | CLOSE | CLOSE | CLOSE | CLOSE
S8200 | SET STATE | 设置状态 Set state | CLOSE | CLOSE | CLOSE | CLOSE
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_PT_DP_SP | yes | Set piont of perssure for vessel draining | real | bar | 0.5 | 0 | 1
| R_WT_SP | yes | Set piont of vessel weight | real | kg | 20 | 0 | 1000
| R_LT_SP | yes | Set piont of vessel level | real | L | 20 | 0 | 10000
| R_DRAIN_TM | yes | Delay time of media drain | real | sec | 30 | 0 | 100
| R_PT_RELEASE | yes | Setpoint for releasing tank pressure | real | bar | 0.2 | 0 | 2
| R_S1020_STEP_TM | yes | maximum Drain time of tank and product pipe | real | min | 30 | 0 | 100
| R_PT_DP_SP_DEV | yes | Devation of perssure for vessel draining | real | bar | 0.1 | 0 | 1
11. | Report Parameter (RP) Table
| Parameter |  | Description |  | Eng.Unit | Step | Begin | End
| NA |  | NA |  | NA | NA | NA | NA
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXBP01 Emergency Stop is Only for Buffer Preparation Tank Uint Class
| Hold03 |  | E-DSXBH01 Emergency Stop is Only for Buffer Holding Tank Uint Class
| Hold04 |  | WIT/LIT Fault

## ALARM (hidden)
INDICATION | S150~S180