## Cover Sheet
Phase Specification
PH_C_BP
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-001610 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_.....
| Step | max. 16 characters, _ for delimiter
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-16 | 杜林茂 | Draft
杜林茂
杜林茂
杜林茂
| 0.1a | 2020-10-28 | 杜林茂 | Updated according to comments
| 0.1a | 2020-10-29 | 杜林茂
| 0.1a | 2020-10-30 | 杜林茂
| 0.1b | 2020-11-10 | 杜林茂 | 1. Description: 7.2 Equipment Module中EM_AG_01改为AG01 2. SFC_RUN： S1010删除计时报警； S1020更新计时报警参数名称； S1030更新transition条件参数名称以及计时报警参数名称； S1040更新step名称以及transition参数名称； S1050更新计时报警参数名称； S1070增加计时报警； S1100更新transition条件参数名称； 3. Action Table： 用AG01取代EM_BUF_AG，并更新相应实例； 增加EM_BUF_CIPR及相关EM实例和Command； 更新S1040名称和Other Action； EM_C_BTH中VENT_FA改为WT_FILTER_OPEN; EM_C_RTN中RTN_DRN改为RTN_DR； 更新S1020，S1030，S1050中Alarm Settings； 更新S1070中Alarm Settings和Other Actions； 更新Note 6，7，9 4. ParameterHold Tables： R_TM_MIX改为R_TM_AG; 增加参数R_WFI_TOC_SP； R_Speed_Mixer改为R_Speed_AG; 更新R_MAX_TM_STEP1-4描述; 删除R_Flow_SP_CIPR，增加L_FLOW_CIPR_PV
| 0.1c | 2020-11-18 | 杜林茂 | 1. Action Table: S1030，S1060增加“Record FIT01”； S1080增加Other Action的描述； 2. ParameterHold Tables Input Parameter (IP) Table参数命名中涉及“Speed”均改为SPD； Input Parameter (IP) Table参数命名中R_ALK_VOL改为R_ALK_TM； Report Parameter (RP) Table增加L_FLOW_CIPS_PV和L_WFI_TOC_PV
| 0.1d | 2020-11-20 | 杜林茂 | 1. SFC_RUN: 增加路径参数名称 2. SFC_HOLD_ABORT: 删除S7000和S8000 3. Action Table： 增加路径参数名称； 更新S1120对应EM_C_RTN的Command； 删除S7000和S8000，并在S7010和S8010增加Other Actions； 将ABORT中Command改为CLOSE 4. ParameterHold Tables: 增加路径参数名称
| 0.1e | 2020-12-09 | 杜林茂 | 1. SFC_RUN: WFI清洗检测策略修改，电导与TOC同时检测，见顺控图； 增加Note3&4 2. Action Table： 更新S1060，S1070，删除S1080 3. ParameterHold Tables: 删除R_MAX_TM_STEP4； 更新R_TM_CT和R_TM_TOC设定值； 增加Report参数L_CT_CHECK和L_TOC_CHECK； 更新HOLD Table
| 1 | 2021-03-03 | 杜林茂 | 根据仿真测试修改
| 2 | 2021-04-12 | 杜林茂 | 增加急停编号
| 2.0b | 2021-06-05 | 王树深 | 修改PW清洗回罐和排放策略;修改prep medium时管道状态；修改急停策略
| 2.0c | 2021-06-17 | 王树深 | 增加参数
| 2.0d | 2021-06-28 | 王树深 | 修改S1020的E_CIP_RTN的command为STOP
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase C_BP is used for CIP BP tank. Phase at CIP object performs control actions for cleaning of CIP object and controls CIP return pump.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| BP Tank | 3000L BUFFER PREPARATION TANK UNIT TA12
3000L BUFFER PREPARATION TANK UNIT TA13
6000L BUFFER PREPARATION TANK UNIT TA14
9000L BUFFER PREPARATION TANK UNIT TA15
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| BP Tank | EM_BP_TOP
EM_BP_HEAD
EM_BP_BOM
EM_BP_FA
AG01
EM_BUF_CIPS
EM_BUF_CIPR
EM_BUF_CIPR_PU
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| CIP Station | EM_C_CIP
EM_C_SUP
EM_C_RTN
EM_C_BTH
EM_BCIP_CIPS
EM_BCIP_CIPR

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | RUN Logic with Check Steps
| Note1: | R_SELECT_STATION is 03 or 05. Default of R_SELECT_STATION can be modified.
If R_SELECT_STATION is 03, select CIP03 if CIP03 is standby. Select CIP05 if CIP03 is occupied.

## SFC_RUN
8. | RUN Logic with Check Steps
|  | Phase (Note2) | Note2
|  | R_C_DSXTA12_SEL | WIT-DSXTA1301C
|  | R_C_DSXTA13_SEL | WIT-DSXTA1301B
|  | R_C_DSXTA14_SEL | WIT-DSXTA1501C
|  | R_C_DSXTA15_SEL | WIT-DSXTA1501B
Note1 | Current Medium will be judged by the logic,according to the parameter CIP_Medium1/CIP_Medium2/CIP_Medium3/CIP_Medium4
Note2 | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
Note3 | CHECK_CT and CHECK_TOC finished
Note4 | Check CT and TOC simultaneously at the start of S1070.
For CHECK_CT:
1) If AIT03 > R_WFI_CT_SP, then CHECK_CT=FAILED. If AIT03 < R_WFI_CT_SP, then enable Timer R_TM_CT.
2) If AIT03 < R_WFI_CT_SP and R_TM_CT is elapsed, then CHECK_CT=PASSED.
If AIT03 > R_WFI_CT_SP during R_TM_CT, then CHECK_CT=FAILED.
For CHECK_TOC:
1) If QIT01 > R_WFI_TOC_SP, then CHECK_TOC=FAILED. If QIT01 < R_WFI_TOC_SP, then enable Timer R_TM_TOC.
2) If QIT01 < R_WFI_TOC_SP and R_TM_TOC is elapsed, then CHECK_TOC=PASSED.
If QIT01 > R_WFI_TOC_SP during R_TM_TOC, then CHECK_TOC=FAILED.
Alarm if CHECK_CT=FAILED or CHECK_TOC=FAILED.
预留TOC检测功能，该phase须能保证在无TOC检测的情况下正常运行。

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution.
Unit Class |  | Phase
Buffer Preparation System |  | PH_C_DSXTA12 | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note10) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | EM_DSXBP_CIPS | EM_DSXTA12_HEAD | EM_DSXTA12_TOP | EM_DSXTA12_FA | AG_DSXTA1201 | EM_DSXTA12_BOM | EM_DSXBP_CIPR | EM_DSXBP_CIPRPU | EM_DSXCIP03_CIPR/EM_DSXCIP05_CIPR (Note4) | EM_DSXCIP03_RTN/EM_DSXCIP05_RTN (Note5)
|  | PH_C_DSXTA13 | [5 empty] | EM_DSXTA13_HEAD | EM_DSXTA13_TOP | EM_DSXTA13_FA | AG_DSXTA1301 | EM_DSXTA13_BOM
|  | PH_C_DSXTA14 | [5 empty] | EM_DSXTA14_HEAD | EM_DSXTA14_TOP | EM_DSXTA14_FA | AG_DSXTA1401 | EM_DSXTA14_BOM
|  | PH_C_DSXTA15 | [5 empty] | EM_DSXTA15_HEAD | EM_DSXTA15_TOP | EM_DSXTA15_FA | AG_DSXTA1501 | EM_DSXTA15_BOM
Step |  | Description | EM_C_CIP | EM_C_SUP | EM_C_BTH | EM_BCIP_CIPS | EM_BUF_CIPS | EM_BP_HEAD | EM_BP_TOP | EM_BP_FA | AG01 | EM_BP_BOM | EM_BUF_CIPR | EM_BUF_CIPR_PU | EM_BCIP_CIPR | EM_C_RTN | Report Record | Alarm Settings | Controller Settings | Other Actions
S9000 | STATION_CHECK | 检查CIP站的占用状态 Check the occupation of CIP stations. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | MESSAGE | 提示是否放弃 Prompt to abort the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | STATE_CHECK | 状态检查 Check all line and vessel status | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ROUTE_CHECK | 路径检查 Check if all the jumpers are in right position | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9080 | ENABLE HM&SM | 启动程序监测 Enable hold monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S2010 | DEACTIVE | 程序非自结束 Deactive | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | CHECK_MEDIUM | 检查介质 Check medium | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  | Assign value to Current_Medium according to the parameter CIP_Medium1/CIP_Medium2/CIP_Medium3/CIP_Medium4
S1020 | PREP_MEDIUM | 准备介质 CIP station medium preparation | Note6 | STOP | WT_FILTER_OPEN | CIP_TO_TA15 | Note11 | CIP_TK | CIP_TK | SIP_FA | STOP | CIP_TK | Note8 | STOP | CIP_FR_TA15 | STOP |  | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP1
S1030 | FILLING | 加水 Add water into tank | Note7 | MEDIUM_SUPPLY | WT_FILTER_OPEN | CIP_TO_TA15 | Note11 | CIP_TK | CIP_IN | VENT_FA | STOP | CLOSE | CLOSE | STOP | CLOSE | STOP |  | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP2
S1040 | AGITATION | 清洗搅拌 Clean mixer | STOP | MEDIUM_SUPPLY | WT_FILTER_OPEN | CIP_TO_TA15 | CLOSE | CIP_TK | CIP_IN | VENT_FA | START | CLOSE | CLOSE | STOP | CLOSE | STOP
S1050 | DRAIN1 | 排放 Drain tank | STOP | MEDIUM_SUPPLY | WT_FILTER_OPEN | CIP_TO_TA15 | Note11 | CIP_TK | CIP_IN | VENT_FA | STOP | CIP_TK | Note8 | PU_ON | CIP_FR_TA15 | Note9 |  | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP3
S1060 | CIP_TK | 清洗喷淋球 CIP tank by spray ball | Note7 | MEDIUM_SUPPLY | WT_FILTER_OPEN | CIP_TO_TA15 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | STOP | CIP_TK | Note8 | PU_ON | CIP_FR_TA15 | Note9
S1070 | CHECK_CT_TOC | 电导和TOC检测 Check CT and TOC | Note7 | MEDIUM_SUPPLY | WT_FILTER_OPEN | CIP_TO_TA15 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | STOP | CIP_TK | Note8 | PU_ON | CIP_FR_TA15 | RTN_TOC | Record AIT03 Record QIT01 |  |  | If Medium is WFI, record AIT03 and QIT01. Record result of S1070: CHECK_CT=PASSED or FAILED CHECK_TOC=PASSED or FAILED
S1090 | STOP_PUMP | 停泵 Stop CIPR pump | STOP_PUMP | MEDIUM_SUPPLY | WT_FILTER_OPEN | CIP_TO_TA15 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | STOP | CIP_TK | Note8 | STOP | CIP_FR_TA15 | Note9
S1100 | BLOW_TK | 吹扫喷淋球 Blow tank by spray ball | STOP | AIR_BLOW | WT_FILTER_OPEN | CIP_TO_TA15 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | STOP | CIP_TK | Note8 | STOP | CIP_FR_TA15 | Note9
S1110 | FINAL_CHECK | 最终确认 Check final medium. | STOP | STOP | WT_FILTER_OPEN | CIP_TO_TA15 | Note11 | CIP_TK | CIP_TK | PW_ALK_FA | STOP | CIP_TK | Note8 | STOP | CIP_FR_TA15 | Note9
S1120 | BLOW_LP | 吹扫低点 Blow low point | STOP | AIRBLOW_LP | WT_FILTER_OPEN | CIP_TO_TA15 | Note11 | CIP_TK | CIP_TK | WFI_PA_FA | STOP | CIP_TK_PUL_DRN | Note8 | PU_OFF_DRN | CIP_FR_TA15 | RTN_LP_DR
S1130 | CLOSE | 关闭所有设备 Close all device | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | VENT_FA | STOP | CLOSE | CLOSE | STOP | CLOSE | CLOSE |  |  |  | If CHECK_CT&CHECK_TOC=PASSED, go to S1140. If CHECK_CT&CHECK_TOC=FAILED, end the phase.
S1140 | SET_STATE | 重置状态 Set state | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | VENT_FA | STOP | CLOSE | CLOSE | STOP | CLOSE | CLOSE |  |  |  | Set state to CLEAN
S7010 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD |  |  |  | First to HOLD EM_C_CIP and EM_BUF_CIPR_PU, then ohrers
S8010 | ABORT | 中止步骤 Abort | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | CLOSE | CLOSE | STOP | CLOSE | CLOSE |  |  |  | First to STOP EM_C_CIP and EM_BUF_CIPR_PU, then ohrers
S8030 | SET_STATE | 重置状态 Set state | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | CLOSE | CLOSE | STOP | CLOSE | CLOSE |  |  |  | Set state to DIRTY
Note1: If select CIP03 station, EM will be EM_DSXCIP03. If select CIP05 station, EM will be EM_DSXCIP05.
Note2: If select CIP03 station, EM will be EM_DSXCIP03_SUP. If select CIP05 station, EM will be EM_DSXCIP05_SUP.
Note3: If select CIP03 station, EM will be EM_DSXCIP03_CIPS. If select CIP05 station, EM will be EM_DSXCIP05_CIPS.
Note4: If select CIP03 station, EM will be EM_DSXCIP03_CIPR. If select CIP05 station, EM will be EM_DSXCIP05_CIPR.
Note5: If select CIP03 station, EM will be EM_DSXCIP03_RTN. If select CIP05 station, EM will be EM_DSXCIP05_RTN.
Note6: If medium is PW, use PREP_PW. If medium is ALKALI, use PREP_ALK. If medium is WFI, use PREP_WFI.
Note7: If medium is PW, use SUPPLY_PW. If medium is ALKALI, use SUPPLY_ALK. If medium is WFI, use SUPPLU_WFI.
Note8: If phase= DSXTA12, command is CIPR_FR_12. If phase= DSXTA13, command is CIPR_FR_13. If phase= DSXTA14, command is CIPR_FR_14. If phase= DSXTA15, N/A
Note9: If medium is PW in CIP_Medium1,use RTN_DR_NP; if medium is PW in CIP_Medium3,use RTN_DR. If medium is ALKALI, use RTN_TK. If medium is WFI, use RTN_TOC.
Note10: If select CIP03 station, EM will be EM_DSXCIP03_BTH. If select CIP05 station, EM will be EM_DSXCIP05_BTH.
Note11: If phase= DSXTA12, command is CIP_TO_TA12. If phase= DSXTA13, command is CIP_TO_TA13. If phase= DSXTA14, command is CIP_TO_TA14. If phase= DSXTA15, N/A.
"X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| CIP_Medium1 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_Medium2 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_Medium3 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_Medium4 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| R_SELECT_STATION | NO | Preferred CIP Station selected | N/A | N/A | CIP03 or CIP05 | N/A | N/A
| R_TM_CIP_PW | YES | CIP time for tank by PW | real | min | 5 | 0 | 60
| R_TM_CIP_ALK | YES | CIP time for tank by ALK | real | min | 20 | 0 | 60
| R_TM_CIP_WFI | YES | CIP time for tank_WFI | real | min | 5 | 0 | 60
| R_TM_AG_PW | YES | CIP time for agitation with PW | real | min | 5 | 0 | 10
| R_TM_AG_ALK | YES | CIP time for agitation with ALK | real | min | 5 | 0 | 10
| R_TM_AG_WFI | YES | CIP time for agitation with WFI | real | min | 5 | 0 | 10
| R_TM_CT | NO | Conductivity check duration | int | sec | 60 | 0 | 600
| R_TM_TOC | NO | TOC check duration | int | sec | 60 | 0 | 600
| R_TM_BLOW_PW | YES | Blow time after PW flush | real | min | 5 | 0 | 10
| R_TM_BLOW_ALK | YES | Blow time after ALK flush | real | min | 5 | 0 | 10
| R_TM_BLOW_WFI | YES | Blow time after WFI flush | real | min | 5 | 0 | 10
| R_TM_BLOW_LP | YES | Blow time after WFI flush | real | min | 5 | 0 | 10
| R_MAX_TM_STEP1 | NO | Maximum step execution time for PREP_MEDIUM, hold if exceed the time | real | min | 30 | 0 | 120
| R_MAX_TM_STEP2 | NO | Maximum step execution time for FILLING, hold if exceed the time | real | min | 30 | 0 | 120
| R_MAX_TM_STEP3 | NO | Maximum step execution time for DRAIN1, hold if exceed the time | real | min | 30 | 0 | 120
| R_Level_AG_RUN | YES | Level agitator can start | real | kg | 350 | 0 | 1000
| R_Level_Empty | NO | Level to stop pump when Drain tank | real | kg | 10 | 0 | 100
| R_WFI_CT_SP | NO | Qualified CT | real | µS/cm | 5 | 0 | 5
| R_WFI_TOC_SP | YES | TOC judgment setpoint | real | ppb | 1000 | 0 | 2000
| R_SPD_SUP_PU | YES | Speed of supply pump | real | Hz | 35 | 0 | 50
| R_SPD_RTN_PU | NO | Speed of return pump | real | Hz | 45 | 0 | 50
| R_SPD_AG | YES | Speed of agitator | real | rpm | 600 | 0 | 1400
| R_ALK_TEMP | YES | Alkali temperature | real | °C | 80 | 0 | 100
| R_ALK_TM | YES | Alkali preparation time | int | sec | 20 | 1 | 180
| R_ALK_PRE_CT | YES | Alkali preparation CT | real | mS/cm | 18 | 0 | 30
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_WFI_CT_PV |  | Process value of conductivity recorded | real | µS/cm | 1070 | N/A | N/A
| L_WFI_TOC_PV |  | Process value of TOC check | real | ppb | 1070 | N/A | N/A
| L_CT_CHECK |  | CHECK_CT is PASSED or FAILED | Nameset | N/A | 1070 | N/A | N/A
| L_TOC_CHECK |  | CHECK_TOC is PASSED or FAILED | Nameset | N/A | 1070 | N/A | N/A
| FE-DSXCIP0301/FE-DSXCIP0501 |  | CIP supply pump flowrate curve | real | m3/h | N/A | N/A | N/A
| AIT-DSXCIP0303/AIT-DSXCIP0503 |  | Conductivity curve during WFI flush | real | µS/cm | N/A | N/A | N/A
| QIT-DSXCIP0301/QIT-DSXCIP0501 |  | TOC curve during WFI flush | real | ppb | N/A | N/A | N/A
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXCIP02/E-DSXBP01 Emergency Stop
| Hold03 |  | CIP station Hold
| Hold04 |  | R_MAX_TM_STEP is elapsed
| Hold05 |  | BP tank WIT fault
| Hold06 |  | AG01 fault

## ALARM (hidden)
INDICATION | S150~S180