## Cover Sheet
Phase Specification PH_S_BH_POU_DS1_3
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-001635 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-25 | 刘会莹 | draft
| 0.1a | 2020-10-29 | 刘会莹 | Update according to comments
| 0.1b | 2020-11-09 | 刘会莹 | Update according to comments
| 0.1c | 2020-11-17 | 刘会莹 | 补充超滤EM
| 0.1d | 2020-11-20 | 刘会莹 | abort命令更新
| 0.1e | 2020-12-04 | 杜林茂 | 1. Description： 补充遗漏的Unit：6000L BUFFER HOLDING TANK UNIT TA31 2. Action Table: 拆分EM_DF03和EM_DF04; 拆分EM_DF03_FILT和EM_VF01_FILT 3. ParameterHold Tables: 更新HOLD Table
| 1.0 | 2021-03-18 | 王树深 | 程序仿真修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号
| 2.0b | 2021-06-02 | 王树深 | 增加上下游信号交互
| 2.0c | 2021-06-05 | 王树深 | 更新急停策略
| 2.0d | 2021-06-28 | 王树深 | 更新信号交互
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase PH_S_BH_POU is used for Sterilization of transfer pipe from Buffer holding Tank to point of use . 1. Monitoring of all condensate temperatures in sterilization step and resetting of sterilization timer if one of the temperatures DRNop SIP_SET_TT.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| BH Tank | DSXTA16
DSXTA17
DSXTA18
DSXTA19
DSXTA21
DSXTA22
DSXTA23
DSXTA24
DSXTA27
DSXTA28
DSXTA29
DSXTA30
DSXTA31
DSXTA33
DSXTA34
DSXTA35
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| BH Tank | EM_BUF_CS
EM_BH_HEAD
EM_BH_BOM
EM_BH_DIS
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| Purfication Tank | EM_CHT_BUF_IN
EM_CHT_DRN
EM_PUR_PD_IN
EM_PUR_TOP
EM_DF03
EM_DF04
EM_DF03_FILT
EM_VF01_FILT
EM_VF01_IN_DIS
EM_UF_BUF_IN
EM_UF_SHARED

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN
8. | RUN Logic without Check Steps
|  | Phase | Note2
|  | Phase: SIP_TA17-CHT01 | TT-DSXTA1704A | TT-DSXCHT0101
|  | Phase: SIP_TA18-CHT01 | TT-DSXTA1604B | TT-DSXCHT0101
|  | Phase: SIP_TA19-CHT01 | TT-DSXTA1704B | TT-DSXCHT0101
|  | Phase: SIP_TA27-CHT01 | TT-DSXTA2604B | TT-DSXCHT0101
|  | Phase: SIP_TA23-CHT03 | TT-DSXTA2104B | TT-DSXCHT0301
|  | Phase: SIP_TA28-CHT02 | TT-DSXTA2804A | TT-DSXCHT0201
|  | Phase: SIP_TA22-CHT03 | TT-DSXTA2204A | TT-DSXCHT0301
|  | Phase: SIP_TA22-CHT02 | TT-DSXTA2204A | TT-DSXCHT0201
|  | Phase: SIP_TA24-CHT03 | TT-DSXTA2204B | TT-DSXCHT0301
|  | Phase: SIP_TA29-CHT02 | TT-DSXTA2804B | TT-DSXCHT0201
|  | Phase: SIP_TA34-CHT01 | TT-DSXTA3404A | TT-DSXCHT0101
|  | Phase: SIP_TA34-CHT02 | TT-DSXTA3404A | TT-DSXCHT0201
|  | Phase: SIP_TA35-CHT03 | TT-DSXTA3404B | TT-DSXCHT0301
|  | Phase: SIP_TA35-TA05 | TT-DSXTA3404B | TT-DSXTA0505
|  | Phase: SIP_TA21-TA03 | TT-DSXTA2104A | TT-DSXTA0305
|  | Phase: SIP_TA29-TA04 | TT-DSXTA2804B | TT-DSXTA0405
|  | Phase: SIP_TA30-TA06 | TT-DSXTA3004A | TT-DSXTA0605
|  | Phase: SIP_TA21-DF03 | TT-DSXTA2104A | TT-DSXDF0301 | TT-DSXDF0302
|  | Phase: SIP_TA34-DF03 | TT-DSXTA3404A | TT-DSXDF0301 | TT-DSXDF0302
|  | Phase: SIP_TA30-NF01 | TT-DSXTA3004A | TT-DSXNF0102 | TT-DSXNF0103
|  | Phase: SIP_TA24-UF01 | TT-DSXTA2204B | TT-DSXUF01-502
|  | Phase: SIP_TA30-UF02 | TT-DSXTA3004A | TT-DSXUF02-502
|  | Phase: SIP_TA31-UF02 | TT-DSXTA3104A | TT-DSXUF02-502
|  | Phase: SIP_TA16-TA01 | TT-DSXTA1604A |  | TT-DSX_Pipe_Temp
|  | Phase: SIP_TA33-TA01 | TT-DSXTA3204B |  | TT-DSX_Pipe_Temp
|  | Phase: SIP_TA16-CHT01 | TT-DSXTA1604A | TT-DSXCHT0101
|  | Phase: SIP_TA33-CHT01 | TT-DSXTA3204B | TT-DSXCHT0101

## SFC_HOLD_ABORT_STOP
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase | EM
|  | Phase: SIP_TA16_TA01 | EM_DSXBH3_CS | EM_DSXTA16_HEAD | EM_DSXTA16_BOM | EM_DSXTA16_DIS | PV-DSXTA1623 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA33_TA01 | EM_DSXBH1_CS | EM_DSXTA33_HEAD | EM_DSXTA33_BOM | N/A | PV-DSXTA3203 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA16_CHT01 | EM_DSXBH3_CS | EM_DSXTA16_HEAD | EM_DSXTA16_BOM | EM_DSXTA16_DIS | N/A | EM_DSXCHT01TA33 | EM_DSXCHT01_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA33_CHT01 | EM_DSXBH1_CS | EM_DSXTA33_HEAD | EM_DSXTA33_BOM | N/A | N/A | EM_DSXCHT01TA33 | EM_DSXCHT01_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA17_CHT01 | EM_DSXBH4_CS | EM_DSXTA17_HEAD | EM_DSXTA17_BOM | N/A | N/A | EM_DSXCHT01TA17 | EM_DSXCHT01_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA18_CHT01 | EM_DSXBH3_CS | EM_DSXTA18_HEAD | EM_DSXTA18_BOM | N/A | N/A | EM_DSXCHT01TA18 | EM_DSXCHT01_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA19_CHT01 | EM_DSXBH4_CS | EM_DSXTA19_HEAD | EM_DSXTA19_BOM | N/A | N/A | EM_DSXCHT01TA19 | EM_DSXCHT01_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA27_CHT01 | EM_DSXBH2_CS | EM_DSXTA27_HEAD | EM_DSXTA27_BOM | N/A | N/A | EM_DSXCHT01TA27 | EM_DSXCHT01_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA23_CHT03 | EM_DSXBH4_CS | EM_DSXTA23_HEAD | EM_DSXTA23_BOM | N/A | N/A | EM_DSXCHT03TA23 | EM_DSXCHT03_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA28_CHT02 | EM_DSXBH2_CS | EM_DSXTA28_HEAD | EM_DSXTA28_BOM | N/A | N/A | EM_DSXCHT02TA28 | EM_DSXCHT02_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA22_CHT02 | EM_DSXBH3_CS | EM_DSXTA22_HEAD | EM_DSXTA22_BOM | N/A | N/A | EM_DSXCHT02TA22 | EM_DSXCHT02_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA22_CHT03 | EM_DSXBH3_CS | EM_DSXTA22_HEAD | EM_DSXTA22_BOM | N/A | N/A | EM_DSXCHT03TA22 | EM_DSXCHT03_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA24_CHT03 | EM_DSXBH3_CS | EM_DSXTA24_HEAD | EM_DSXTA24_BOM | N/A | N/A | EM_DSXCHT03TA24 | EM_DSXCHT03_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA29_CHT02 | EM_DSXBH2_CS | EM_DSXTA29_HEAD | EM_DSXTA29_BOM | N/A | N/A | EM_DSXCHT02TA29 | EM_DSXCHT02_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA34_CHT01 | EM_DSXBH1_CS | EM_DSXTA34_HEAD | EM_DSXTA34_BOM | EM_DSXTA34_DIS | N/A | EM_DSXCHT01TA34 | EM_DSXCHT01_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA34_CHT02 | EM_DSXBH1_CS | EM_DSXTA34_HEAD | EM_DSXTA34_BOM | EM_DSXTA34_DIS | N/A | EM_DSXCHT02TA34 | EM_DSXCHT02_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA35_CHT03 | EM_DSXBH1_CS | EM_DSXTA35_HEAD | EM_DSXTA35_BOM | N/A | N/A | EM_DSXCHT03TA35 | EM_DSXCHT03_DRN | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA21_TA03 | EM_DSXBH4_CS | EM_DSXTA21_HEAD | EM_DSXTA21_BOM | N/A | N/A | N/A | N/A | EM_DSXTA03_PD_IN | EM_DSXTA03_TOP | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA29_TA04 | EM_DSXBH2_CS | EM_DSXTA29_HEAD | EM_DSXTA29_BOM | N/A | N/A | N/A | N/A | EM_DSXTA04_PD_IN | EM_DSXTA04_TOP | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA30_TA06 | EM_DSXBH4_CS | EM_DSXTA30_HEAD | EM_DSXTA30_BOM | EM_DSXTA30_DIS | N/A | N/A | N/A | EM_DSXTA06_PD_IN | EM_DSXTA06_TOP | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA35_TA05 | EM_DSXBH1_CS | EM_DSXTA35_HEAD | EM_DSXTA35_BOM | N/A | N/A | N/A | N/A | EM_DSXTA05_PD_IN | EM_DSXTA05_TOP | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA21_DF03 | EM_DSXBH4_CS | EM_DSXTA21_HEAD | EM_DSXTA21_BOM | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXDF03 | N/A | EM_FDSXDF0301 | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA34_DF03 | EM_DSXBH1_CS | EM_DSXTA34_HEAD | EM_DSXTA34_BOM | EM_DSXTA34_DIS | N/A | N/A | N/A | N/A | N/A | EM_DSXDF03 | N/A | EM_FDSXDF0301 | N/A | N/A | N/A | N/A
|  | Phase: SIP_TA30_NF01 | EM_DSXBH4_CS | EM_DSXTA30_HEAD | EM_DSXTA30_BOM | EM_DSXTA30_DIS | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXDF04 | N/A | EM_FDSXVF0101 | EM_DSXVF01IN_DIS | N/A | N/A
|  | Phase: SIP_TA24_UF01(Note4) | EM_DSXBH3_CS | EM_DSXTA24_HEAD | EM_DSXTA24_BOM | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSYUF01_BUFIN | EM_DSYUF01SHARED
|  | Phase: SIP_TA30_UF02(Note4) | EM_DSXBH4_CS | EM_DSXTA30_HEAD | EM_DSXTA30_BOM | EM_DSXTA30_DIS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSYUF02_BUFIN | EM_DSYUF02SHARED
|  | Phase: SIP_TA31_UF02(Note4) | EM_DSXBH2_CS | EM_DSXTA31_HEAD | EM_DSXTA31_BOM | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSYUF02_BUFIN | EM_DSYUF02SHARED
Step |  | Description | EM_BUF_CS | EM_BH_HEAD | EM_BH_BOM | EM_BH_DIS | CM | EM_CHT_BUF_IN | EM_CHT_DRN | EM_PUR_PD_IN | EM_PUR_TOP | EM_DF03 | EM_DF04 | EM_DF03_FILT | EM_VF01_FILT | EM_VF01_IN_DIS | EM_UF_BUF_IN | EM_UF_SHARED | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 check if all the EM are free or not | N/A | N/A | N/A |  |  | N/A | N/A | N/A | N/A | [9 empty] | Send DSX_BU_SIP_Req=1, Confirm DSX_BU_SIP_Rdy=1 (Note5)
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 prompt to continue or complete the phase | N/A | N/A | N/A |  |  | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A |  |  | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A |  |  | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A |  |  | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A |  |  | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A |  |  | N/A | N/A | N/A | N/A
S1010 | PRE-HEAT | 管道通入纯蒸汽加热，打开排放旁路，排除凝水，管道继续升温。 Heat pipe by clean steam and DRNain condensate water by bypass valve. | CS_SUPPLY | SIP_PE | SIP_PE | Note 1 | OPEN | BUF_IN_CIP | PE_SIP_BPS | BUF_TO_TK | SIP_PD_IN_BPS1 | Note 2 | Note 2 | BUF_IN_SIP_BPS | BUF_IN_SIP_BPS | C_S_PE | Note 3 | BUF_IN_HEAT |  | SP: EM_BUF_CS_PIC OUT= R_CS_PT_SP1
S1020 | HEAT | 管道通入纯蒸汽加热，只通过疏水阀排除凝水，罐体继续升温。 Heat pipe by clean steam and DRNain by steam trap valve. | CS_SUPPLY | SIP_PE | SIP_PE | Note 1 | OPEN | BUF_IN_CIP | PE_SIP | BUF_TO_TK | SIP_PD_IN_PE1 | Note 2 | Note 2 | BUF_IN_SIP | BUF_IN_SIP | C_S_PE | Note 3 | BUF_IN_SIP |  | SP: EM_BUF_CS_PIC OUT= R_CS_PT_SP2
S1030 | STERILIZE | 灭菌计时 Sterilize timer. | CS_SUPPLY | SIP_PE | SIP_PE | Note 1 | OPEN | BUF_IN_CIP | PE_SIP | BUF_TO_TK | SIP_PD_IN_PE1 | Note 2 | Note 2 | BUF_IN_SIP | BUF_IN_SIP | C_S_PE | Note 3 | BUF_IN_SIP
S1040 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Release EM:EM_DSXBH_CS Send DSX_BU_SIP_Req=0, Send DSX_BU_SIP_Fini_Req=1, Confirm DSX_BU_SIP_Fini_Rdy=1 (Note5)
S1050 | SET_STATE | 状态变更 Set State | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Change the state to SIPed
S1200 | REHEAT | 重新加热通过加入纯蒸汽。 Reheat tank by into clean stean. | CS_SUPPLY | SIP_PE | SIP_PE | Note 1 | OPEN | BUF_IN_CIP | PE_SIP | BUF_TO_TK | SIP_PD_IN_PE1 | Note 2 | Note 2 | BUF_IN_SIP | BUF_IN_SIP | C_S_PE | Note 3 | BUF_IN_SIP |  | SP: EM_BUF_CS_PIC OUT= R_CS_PT_SP1 | Send DSX_BU_SIP_Req=1, Confirm DSX_BU_SIP_Rdy=1 (Note5)
S7000 | HOLD | 暂停 pause | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD |  |  | Send DSX_BU_SIP_Req=0,
S8010 | ABORT | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  | CLOSE | CLOSE |  |  | Release EM:EM_DSXBH_CS Send DSX_BU_SIP_Req=0,
S8020 | SET_STATE | 状态变更 Set State | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  | CLOSE | CLOSE |  |  | Change the state to Clean.
|  | Phase | Note 1
|  | Phase: SIP_TA16-TA01 | TA16_TO_TA01
|  | Phase: SIP_TA16-CHT01 | TA16_TO_CHT01
|  | Phase: SIP_TA30-TA06 | TA30 _TO_ TA06UF02
|  | Phase: SIP_TA30_NF01 | TA30 _TO_ TA06UF02
|  | Phase: SIP_TA30_UF02 | N/A
|  | Phase: SIP_TA34_CHT01 | TA34 _TO_ CHT01_02
|  | Phase: SIP_TA34_CHT02 | N/A
|  | Phase: SIP_TA34_DF03 | TA34 _TO_ CHT01_02
|  | Phase | Note 2
|  | Phase: SIP_TA21-DF03 | BUF_FR_TA21_DRN
|  | Phase: SIP_TA30-NF01 | BUF_FR_TA30_DRN
|  | Phase: SIP_TA34-DF03 | BUF_FR_TA34_DRN
|  | Phase | Note 3
|  | Phase: SIP_TA24-UF01 | BUF_FR_TA24
|  | Phase: SIP_TA30-UF02 | BUF_FR_TA30
|  | Phase: SIP_TA31-UF02 | BUF_FR_TA31
Note4：These phases only existed in DS1 and DS3."Y" in "DSY" represents Line number. "Y" can be 1, 3。"Z" in "DSZ" represents Line number. "Z" can be 2, 4
Note5：This signal interaction only uesd for Phase: SIP_TA16_TA01 or SIP_TA33_TA01.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_CS_PT_SP1 | YES | Steam pressure set point for pre-heating pipe | Real | barg | 1.5 | 0 | 2.5
| R_CS_PT_SP2 | YES | Steam pressure set point for sterilize pipe | Real | barg | 1.5 | 0 | 2.5
| R_S1010_STEP_TM | NO | maximum pre-heating time,hold if exceed the time | Real | min | 20 | 2 | 100
| R_S1020_STEP_TM | NO | maximum heating time,hold if exceed the time | Real | min | 20 | 5 | 100
| R_S1040_STEP_TM | NO | maximum heating time,hold if exceed the time | Real | min | 5 | 1 | 100
| R_HEAT_TT_SP | Yes | temperature set point for pre-heating | Real | °C | 95 | 80 | 100
| R_SIP_TT_SP | YES | SIP control temperature | Real | °C | 123 | 121 | 125
| R_SIP_TT_SP_DEV | NO | SIP temperature Deviation | Real | °C | 2 | 0 | 99
| R_STABLE_TM | NO | Stable time | Real | min | 2 | 0 | 10
| R_SIP_TM | YES | SIP time | Real | min | 15 | 0 | 60
| R_TA16_POU_S_SEL | YES | TA16_TA01 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA16_CHT01 | N/A | N/A | N/A | N/A | N/A
| R_TA33_POU_S_SEL | YES | TA33_TA01 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA33_CHT01 | N/A | N/A | N/A | N/A | N/A
| R_TA22_POU_S_SEL | YES | TA22_CHT03 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA22_CHT02 | N/A | N/A | N/A | N/A | N/A
| R_TA24_POU_S_SEL | YES | TA24_CHT03 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA24_DS1&3 UF01 | N/A | N/A | N/A | N/A | N/A
| R_TA34_POU_S_SEL | YES | TA34_CHT01 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA34_CHT02 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA34_DF03 | N/A | N/A | N/A | N/A | N/A
| R_TA35_POU_S_SEL | YES | TA35_CHT03 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA35_TA05 | N/A | N/A | N/A | N/A | N/A
| R_TA21_POU_S_SEL | YES | TA21_TA03 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA21_DF03 | N/A | N/A | N/A | N/A | N/A
| R_TA30_POU_S_SEL | YES | TA30_NF01 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA30_DS1&3 UF02 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA30_TA06 | N/A | N/A | N/A | N/A | N/A
| R_TA29_POU_S_SEL | YES | TA29_CHT02 | N/A | N/A | N/A | N/A | N/A
|  | YES | TA29_TA04 | N/A | N/A | N/A | N/A | N/A
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase Pipe from The defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_SIP_TT_PV |  | Report SIP temperature | Real | °C | S1030 |  | X
| L_SIP_TM |  | Report SIP time | Real | min | S1030 |  | X
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSYPUR01/E-DSYPUR02/E-DSYPUR03/E-DSYPUR04/E-DSYPUR06/E-DSYPUR07/E-DSYBH01 Emergency Stop
| Hold03 |  | Step timer S1010,S1020,S1040 elapsed
| Hold04 |  | Any TT fault
| Hold05 |  | DSX_BF_Alarm_Snd=1 or DSX_BF_Alarm_Rcv=1

## ALARM (hidden)
INDICATION | S150~S180