## Cover Sheet
Phase Specification PH_X_BP_BH
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-001620 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_.....
| Step | max. 16 characters, _ for delimiter
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-25 | 杜林茂 | Draft
| 0.1a | 2020-10-28 | 杜林茂 | Updated based on comments
| 0.1b | 2020-11-20 | 杜林茂 | 1. SFC_CHECK： 更正Note1接近开关位号； 增加TA14到TA32~35传料选项； 增加TA13到TA26·29，TA31传料选项； 增加TA13到SUBAG传料选项； 增加TA12到TA26·29，TA31传料选项； 增加TA12到SUBAG传料选项 2. SFC_RUN: 删除S1030；修改S1050名称；修改S1060名称和条件判断参数名称； 增加S2020，S2030，S2040，S2050 3. Action Table: 删除S1030；修改S1050，S1060名称； 更新S1040对应的Controller Settings描述； 增加EM_BP_SU以及对应Command； TA14，TA13，TA12增加部分选项和对应Command，详见Action Table 4. ParameterHold Tables： 更新R_MAX_TM_STEP1-4参数描述； 新增R_MAX_TM_STEP5； 更新S1060名称和条件判断参数名称； 更新部分参数命名 5. SFC_HOLD_ABORT： 删除S7000和S8000 6. Action Table： 删除S7000和S8000及相关Command； 将HOLD的Command改为CLOSE
| 1.0 | 2021-03-03 | 杜林茂
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号
| 2.0b | 2021-05-25 | 王树深 | 增加压力控制判断上下限，改传料过程中目标罐的状态为VENT
| 2.0c | 2021-06-03 | 王树深 | 取消message提示，改为重量判断
| 2.0d | 2021-06-24 | 王树深 | S2040步EM_BP_DIS改为BUF_DRN
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase _X_BP_BH is used for transferring buffer to buffer holding tank.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Buffer Preparation Tank | 3000L BUFFER PREPARATION TANK UNIT TA12
3000L BUFFER PREPARATION TANK UNIT TA13
6000L BUFFER PREPARATION TANK UNIT TA14
9000L BUFFER PREPARATION TANK UNIT TA15
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Buffer Preparation Tank | EM_BP_BOM
EM_BP_FA
EM_BP_DIS
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| Buffer Holding Tank | EM_BH_TOP
EM_BH_FA
EM_BP_SU

## SFC_CHECK
8. | SFC Check Steps for RUN Logic
NOTE1:
|  | X_TA15_BH | R_CS_SEL1 | From TA15 to TA32 | ZS-DSXTP0101=1
|  |  | R_CS_SEL2 | From TA15 to TA33 | ZS-DSXTP0102=1
|  |  | R_CS_SEL3 | From TA15 to TA34 | ZS-DSXTP0103=1
|  |  | R_CS_SEL4 | From TA15 to TA35 | ZS-DSXTP0104=1
|  |  | R_CS_SEL5 | From TA15 to TA26 | ZS-DSXTP0205=1
|  |  | R_CS_SEL6 | From TA15 to TA27 | ZS-DSXTP0206=1
|  |  | R_CS_SEL7 | From TA15 to TA28 | ZS-DSXTP0207=1
|  |  | R_CS_SEL8 | From TA15 to TA29 | ZS-DSXTP0208=1
|  |  | R_CS_SEL9 | From TA15 to TA31 | ZS-DSXTP0209=1
|  | X_TA14_BH | R_CS_SEL1 | From TA14 to TA32 | ZS-DSXTP0101=1 | ZS-DSXTP0244=1
|  |  | R_CS_SEL2 | From TA14 to TA33 | ZS-DSXTP0102=1 | ZS-DSXTP0244=1
|  |  | R_CS_SEL3 | From TA14 to TA34 | ZS-DSXTP0103=1 | ZS-DSXTP0244=1
|  |  | R_CS_SEL4 | From TA14 to TA35 | ZS-DSXTP0104=1 | ZS-DSXTP0244=1
|  |  | R_CS_SEL5 | From TA14 to TA26 | ZS-DSXTP0210=1
|  |  | R_CS_SEL6 | From TA14 to TA27 | ZS-DSXTP0211=1
|  |  | R_CS_SEL7 | From TA14 to TA28 | ZS-DSXTP0212=1
|  |  | R_CS_SEL8 | From TA14 to TA29 | ZS-DSXTP0213=1
|  |  | R_CS_SEL9 | From TA14 to TA31 | ZS-DSXTP0214=1
|  |  | R_CS_SEL10 | From TA14 to TA16 | ZS-DSXTP0315=1
|  |  | R_CS_SEL11 | From TA14 to TA18 | ZS-DSXTP0316=1
|  |  | R_CS_SEL12 | From TA14 to TA22 | ZS-DSXTP0317=1
|  |  | R_CS_SEL13 | From TA14 to TA24 | ZS-DSXTP0318=1
|  |  | R_CS_SEL14 | From TA14 to TA17 | ZS-DSXTP0319=1
|  |  | R_CS_SEL15 | From TA14 to TA19 | ZS-DSXTP0320=1
|  |  | R_CS_SEL16 | From TA14 to TA21 | ZS-DSXTP0321=1
|  |  | R_CS_SEL17 | From TA14 to TA23 | ZS-DSXTP0322=1
|  |  | R_CS_SEL18 | From TA14 to TA30 | ZS-DSXTP0323=1
|  | X_TA13_BH | R_CS_SEL1 | From TA13 to TA26 | ZS-DSXTP0210=1 | ZS-DSXTP0345=1
|  |  | R_CS_SEL2 | From TA13 to TA27 | ZS-DSXTP0211=1 | ZS-DSXTP0345=1
|  |  | R_CS_SEL3 | From TA13 to TA28 | ZS-DSXTP0212=1 | ZS-DSXTP0345=1
|  |  | R_CS_SEL4 | From TA13 to TA29 | ZS-DSXTP0213=1 | ZS-DSXTP0345=1
|  |  | R_CS_SEL5 | From TA13 to TA31 | ZS-DSXTP0214=1 | ZS-DSXTP0345=1
|  |  | R_CS_SEL6 | From TA13 to TA16 | ZS-DSXTP0324=1
|  |  | R_CS_SEL7 | From TA13 to TA18 | ZS-DSXTP0325=1
|  |  | R_CS_SEL8 | From TA13 to TA22 | ZS-DSXTP0326=1
|  |  | R_CS_SEL9 | From TA13 to TA24 | ZS-DSXTP0327=1
|  |  | R_CS_SEL10 | From TA13 to TA17 | ZS-DSXTP0328=1
|  |  | R_CS_SEL11 | From TA13 to TA19 | ZS-DSXTP0329=1
|  |  | R_CS_SEL12 | From TA13 to TA21 | ZS-DSXTP0330=1
|  |  | R_CS_SEL13 | From TA13 to TA23 | ZS-DSXTP0331=1
|  |  | R_CS_SEL14 | From TA13 to TA30 | ZS-DSXTP0332=1
|  |  | R_CS_SEL15 | From TA13 to SUBAG | ZS-DSXTP0333=1
|  | X_TA12_BH | R_CS_SEL1 | From TA12 to TA26 | ZS-DSXTP0210=1 | ZS-DSXTP0346=1
|  |  | R_CS_SEL2 | From TA12 to TA27 | ZS-DSXTP0211=1 | ZS-DSXTP0346=1
|  |  | R_CS_SEL3 | From TA12 to TA28 | ZS-DSXTP0212=1 | ZS-DSXTP0346=1
|  |  | R_CS_SEL4 | From TA12 to TA29 | ZS-DSXTP0213=1 | ZS-DSXTP0346=1
|  |  | R_CS_SEL5 | From TA12 to TA31 | ZS-DSXTP0214=1 | ZS-DSXTP0346=1
|  |  | R_CS_SEL6 | From TA12 to TA16 | ZS-DSXTP0334=1
|  |  | R_CS_SEL7 | From TA12 to TA18 | ZS-DSXTP0335=1
|  |  | R_CS_SEL8 | From TA12 to TA22 | ZS-DSXTP0336=1
|  |  | R_CS_SEL9 | From TA12 to TA24 | ZS-DSXTP0337=1
|  |  | R_CS_SEL10 | From TA12 to TA17 | ZS-DSXTP0338=1
|  |  | R_CS_SEL11 | From TA12 to TA19 | ZS-DSXTP0339=1
|  |  | R_CS_SEL12 | From TA12 to TA21 | ZS-DSXTP0340=1
|  |  | R_CS_SEL13 | From TA12 to TA23 | ZS-DSXTP0341=1
|  |  | R_CS_SEL14 | From TA12 to TA30 | ZS-DSXTP0342=1
|  |  | R_CS_SEL15 | From TA12 to SUBAG | ZS-DSXTP0343=1

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN
8. | RUN Logic without Check Steps
|  | Phase | BH_LIT(Note1) | BP_PIT(Note2) | BH_PIT(Note3): | BP_WIT(Note4):
|  | X_DSXTA15_BH | LIT-DSXTA3201A | PIT-DSXTA1501B | PIT_DSXTA3201A | WIT_DSXTA1501B
|  |  | LIT-DSXTA3201B |  | PIT_DSXTA3201B
|  |  | LIT-DSXTA3401A |  | PIT_DSXTA3401A
|  |  | LIT-DSXTA3401B |  | PIT_DSXTA3401B
|  | X_DSXTA14_BH | LIT-DSXTA2601A | PIT-DSXTA1401C | PIT_DSXTA2601A | WIT_DSXTA1401C
|  |  | LIT-DSXTA2601B |  | PIT_DSXTA2601B
|  |  | LIT-DSXTA2801A |  | PIT_DSXTA2801A
|  |  | LIT-DSXTA2801B |  | PIT_DSXTA2801B
|  |  | LIT-DSXTA3101A |  | PIT_DSXTA3101A
|  | X_DSXTA13_BH | LIT-DSXTA1601A | PIT-DSXTA1301B | PIT_DSXTA1601A | WIT_DSXTA1301B
|  |  | LIT-DSXTA1601B |  | PIT_DSXTA1601B
|  |  | LIT-DSXTA2201A |  | PIT_DSXTA2201A
|  |  | LIT-DSXTA2201B |  | PIT_DSXTA2201B
|  | X_DSXTA12_BH | LIT-DSXTA1701A | PIT-DSXTA1201C | PIT_DSXTA1701A | WIT_DSXTA1201C
|  |  | LIT-DSXTA1701B |  | PIT_DSXTA1701B
|  |  | LIT-DSXTA2101A |  | PIT_DSXTA2101A
|  |  | LIT-DSXTA2101B |  | PIT_DSXTA2101B
|  |  | LIT-DSXTA3001A |  | PIT_DSXTA3001A
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
| Unit Class | Phase | EM
| PH_X_TA15 | from TA15 to TA32 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A | Note1 | Note2 | N/A
|  | from TA15 to TA33 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A
|  | from TA15 to TA34 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A
|  | from TA15 to TA35 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A
|  | from TA15 to TA26 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A
|  | from TA15 to TA27 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A
|  | from TA15 to TA28 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A
|  | from TA15 to TA29 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A
|  | from TA15 to TA31 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | EM_DSXTP01_DIS | N/A
| PH_X_TA14 | from TA14 to TA32 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | EM_DSXTP01_DIS | EM_DSXTP02_DIS |  |  | N/A
|  | from TA14 to TA33 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | EM_DSXTP01_DIS | EM_DSXTP02_DIS |  |  | N/A
|  | from TA14 to TA34 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | EM_DSXTP01_DIS | EM_DSXTP02_DIS
|  | from TA14 to TA35 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | EM_DSXTP01_DIS | EM_DSXTP02_DIS
|  | from TA14 to TA26 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA27 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA28 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA29 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA31 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA16 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS |  |  | N/A
|  | from TA14 to TA18 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS |  |  | N/A
|  | from TA14 to TA22 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA24 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA17 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA19 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA21 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA23 | EM_DSXTA14_BOM | EM_DSXTA14_FA | EM_DSXTA14_DIS | N/A | EM_DSXTP02_DIS
|  | from TA14 to TA30 | EM_DSXTA15_BOM | EM_DSXTA15_FA | EM_DSXTA15_DIS | N/A | EM_DSXTP02_DIS
| PH_X_TA13 | from TA13 to TA26 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS |  |  | EM_DSXBP_SU
|  | from TA13 to TA27 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS |  |  | N/A
|  | from TA13 to TA28 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS |  |  | N/A
|  | from TA13 to TA29 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS
|  | from TA13 to TA31 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | EM_DSXTP02_DIS
|  | from TA13 to TA16 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A
|  | from TA13 to TA18 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A
|  | from TA13 to TA22 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A
|  | from TA13 to TA24 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A |  |  | EM_DSXBP_SU
|  | from TA13 to TA17 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A |  |  | N/A
|  | from TA13 to TA19 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A |  |  | N/A
|  | from TA13 to TA21 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A
|  | from TA13 to TA23 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A
|  | from TA13 to TA30 | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A
|  | from TA13 to SUBAG | EM_DSXTA13_BOM | EM_DSXTA13_FA | EM_DSXTA13_DIS | N/A | N/A
| PH_X_TA12 | from TA12 to TA26 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS |  |  | EM_DSXBP_SU
|  | from TA12 to TA27 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS |  |  | N/A
|  | from TA12 to TA28 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS |  |  | N/A
|  | from TA12 to TA29 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS
|  | from TA12 to TA31 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | EM_DSXTP02_DIS
|  | from TA12 to TA16 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A
|  | from TA12 to TA18 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A
|  | from TA12 to TA22 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A
|  | from TA12 to TA24 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A |  |  | EM_DSXBP_SU
|  | from TA12 to TA17 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A |  |  | N/A
|  | from TA12 to TA19 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A |  |  | N/A
|  | from TA12 to TA21 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A
|  | from TA12 to TA23 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A
|  | from TA12 to TA30 | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A
|  | from TA12 to SUBAG | EM_DSXTA12_BOM | EM_DSXTA12_FA | EM_DSXTA12_DIS | N/A | N/A
Step |  | Description | EM_BP_BOM | EM_BP_FA | EM_BP_DIS | EM_TP01_DIS | EM_TP02_DIS | EM_BH_TOP | EM_BH_FA | EM_BP_SU | Record Report | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | MESSAGE | 提示是否开始转料 Prompt to transfer buffer | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP1
S1020 | CLEAR_LEVEL | 缓冲液缓存罐液位清零 Clear LIT of BH Tank | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | BH_LIT01 | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP2
S1040 | PRES_CONT1 | 压力控制 Pressure control | CLOSE | PRESSURE_CONT | CLOSE | CLOSE | CLOSE | CLOSE | VENT | N/A |  | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP3 | EM_BP_FA: SP=R_BP_PI_SP △P=R_BP_PI_DEV_SP
S1050 | BUF_X_BH | 缓冲液转移 Buffer transfer | PD_OUT | PRESSURE_CONT | BUF_TS | Note 3 | Note 4 | PD_IN | VENT | N/A |  | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP4;
S1060 | X_DELAY | 延时 Delay | PD_OUT | PRESSURE_CONT | BUF_TS | Note 3 | Note 4 | PD_IN | VENT | N/A
S1070 | FILT_DRN | 过滤器排放 Filter drain | PD_OUT | PRESSURE_CONT | BUF_DRN | Note 3 | Note 4 | PD_IN_DRN | VENT | N/A
S1080 | VENT | 放空 Vent | PD_OUT | VENT_FA | BUF_DRN | Note 3 | Note 4 | PD_IN_DRN | VENT | N/A
S1090 | CLOSE | 关闭所有阀门 Close all valve | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | PRESSURE_CONT | N/A |  |  | EM_BH_FA: SP=R_BH_PI_SP △P=R_BH_PI_DEV_SP
S1100 | SET_STATE | 设置状态 Set state | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | PRESSURE_CONT | N/A |  |  | EM_BH_FA: SP=R_BH_PI_SP △P=R_BH_PI_DEV_SP | Source Tank=Dirty Target Tank = Process Line State = Dirty
S2020 | PRES_CONT2 | 压力控制 Pressure control | CLOSE | PRESSURE_CONT | CLOSE | CLOSE | CLOSE | N/A | N/A | CLOSE |  | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP5 | EM_BP_FA: SP=R_BP_PI_SP △P=R_BP_PI_DEV_SP
S2030 | BUF_X_SUBAG | 缓冲液转移 Buffer transfer | PD_OUT | PRESSURE_CONT | BUF_TS | Note 3 | Note 4 | N/A | N/A | BUF_TO_SU
S2040 | VENT | 放空 Vent | PD_OUT | VENT_FA | BUF_DRN | Note 3 | Note 4 | N/A | N/A | BUF_TO_SU
S2050 | CLOSE | 关闭所有阀门 Close all valve | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | N/A | N/A | CLOSE
S2060 | SET_STATE | 设置状态 Set state | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | N/A | N/A | CLOSE |  |  |  | Source Tank=Dirty Line State = Dirty | 新增
S7010 | HOLD | 暂停 Hold | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S8010 | ABORT | 终止 Abort | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S8020 | SET_STATE | 设置状态 Set state | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  |  | Source Tank:Process Target Tank = Process Line State = Process
|  | Phase | Description | Note1 | Note2 | Note3 | Note4
| PH_X_TA15 | R_CS_SEL1 | from TA15 to TA32 | EM_DSXTA32_TOP | EM_DSXTA32_FA | BUF_TS | N/A
|  | R_CS_SEL2 | from TA15 to TA33 | EM_DSXTA33_TOP | EM_DSXTA33_FA | BUF_TS | N/A
|  | R_CS_SEL3 | from TA15 to TA34 | EM_DSXTA34_TOP | EM_DSXTA34_FA | BUF_TS | N/A
|  | R_CS_SEL4 | from TA15 to TA35 | EM_DSXTA35_TOP | EM_DSXTA35_FA | BUF_TS | N/A
|  | R_CS_SEL5 | from TA15 to TA26 | EM_DSXTA26_TOP | EM_DSXTA26_FA | BUF_TS_1 | N/A
|  | R_CS_SEL6 | from TA15 to TA27 | EM_DSXTA27_TOP | EM_DSXTA27_FA | BUF_TS_1 | N/A
|  | R_CS_SEL7 | from TA15 to TA28 | EM_DSXTA28_TOP | EM_DSXTA28_FA | BUF_TS_1 | N/A
|  | R_CS_SEL8 | from TA15 to TA29 | EM_DSXTA29_TOP | EM_DSXTA29_FA | BUF_TS_1 | N/A
|  | R_CS_SEL9 | from TA15 to TA31 | EM_DSXTA31_TOP | EM_DSXTA31_FA | BUF_TS_1 | N/A
| PH_X_TA14 | R_CS_SEL1 | from TA14 to TA32 | EM_DSXTA32_TOP | EM_DSXTA32_FA | BUF_TS_2 | BUF_TS
|  | R_CS_SEL2 | from TA14 to TA33 | EM_DSXTA33_TOP | EM_DSXTA33_FA | BUF_TS_2 | BUF_TS
|  | R_CS_SEL3 | from TA14 to TA34 | EM_DSXTA34_TOP | EM_DSXTA34_FA | BUF_TS_2 | BUF_TS
|  | R_CS_SEL4 | from TA14 to TA35 | EM_DSXTA35_TOP | EM_DSXTA35_FA | BUF_TS_2 | BUF_TS
|  | R_CS_SEL5 | from TA14 to TA26 | EM_DSXTA26_TOP | EM_DSXTA26_FA | N/A | BUF_TS
|  | R_CS_SEL6 | from TA14 to TA27 | EM_DSXTA27_TOP | EM_DSXTA27_FA | N/A | BUF_TS
|  | R_CS_SEL7 | from TA14 to TA28 | EM_DSXTA28_TOP | EM_DSXTA28_FA | N/A | BUF_TS
|  | R_CS_SEL8 | from TA14 to TA29 | EM_DSXTA29_TOP | EM_DSXTA29_FA | N/A | BUF_TS
|  | R_CS_SEL9 | from TA14 to TA31 | EM_DSXTA31_TOP | EM_DSXTA31_FA | N/A | BUF_TS
|  | R_CS_SEL10 | from TA14 to TA16 | EM_DSXTA16_TOP | EM_DSXTA16_FA | N/A | BUF_TS_1
|  | R_CS_SEL11 | from TA14 to TA18 | EM_DSXTA18_TOP | EM_DSXTA18_FA | N/A | BUF_TS_1
|  | R_CS_SEL12 | from TA14 to TA22 | EM_DSXTA22_TOP | EM_DSXTA22_FA | N/A | BUF_TS_1
|  | R_CS_SEL13 | from TA14 to TA24 | EM_DSXTA24_TOP | EM_DSXTA24_FA | N/A | BUF_TS_1
|  | R_CS_SEL14 | from TA14 to TA17 | EM_DSXTA17_TOP | EM_DSXTA17_FA | N/A | BUF_TS_1
|  | R_CS_SEL15 | from TA14 to TA19 | EM_DSXTA19_TOP | EM_DSXTA19_FA | N/A | BUF_TS_1
|  | R_CS_SEL16 | from TA14 to TA21 | EM_DSXTA21_TOP | EM_DSXTA21_FA | N/A | BUF_TS_1
|  | R_CS_SEL17 | from TA14 to TA23 | EM_DSXTA23_TOP | EM_DSXTA23_FA | N/A | BUF_TS_1
|  | R_CS_SEL18 | from TA14 to TA30 | EM_DSXTA30_TOP | EM_DSXTA30_FA | N/A | BUF_TS_1
| PH_X_TA13 | R_CS_SEL1 | from TA13 to TA26 | EM_DSXTA26_TOP | EM_DSXTA26_FA | N/A | BUF_TS_2
|  | R_CS_SEL2 | from TA13 to TA27 | EM_DSXTA27_TOP | EM_DSXTA27_FA | N/A | BUF_TS_2
|  | R_CS_SEL3 | from TA13 to TA28 | EM_DSXTA28_TOP | EM_DSXTA28_FA | N/A | BUF_TS_2
|  | R_CS_SEL4 | from TA13 to TA29 | EM_DSXTA29_TOP | EM_DSXTA29_FA | N/A | BUF_TS_2
|  | R_CS_SEL5 | from TA13 to TA31 | EM_DSXTA31_TOP | EM_DSXTA31_FA | N/A | BUF_TS_2
|  | R_CS_SEL6 | from TA13 to TA16 | EM_DSXTA16_TOP | EM_DSXTA16_FA | N/A | N/A
|  | R_CS_SEL7 | from TA13 to TA18 | EM_DSXTA18_TOP | EM_DSXTA18_FA | N/A | N/A
|  | R_CS_SEL8 | from TA13 to TA22 | EM_DSXTA22_TOP | EM_DSXTA22_FA | N/A | N/A
|  | R_CS_SEL9 | from TA13 to TA24 | EM_DSXTA24_TOP | EM_DSXTA24_FA | N/A | N/A
|  | R_CS_SEL10 | from TA13 to TA17 | EM_DSXTA17_TOP | EM_DSXTA17_FA | N/A | N/A
|  | R_CS_SEL11 | from TA13 to TA19 | EM_DSXTA19_TOP | EM_DSXTA19_FA | N/A | N/A
|  | R_CS_SEL12 | from TA13 to TA21 | EM_DSXTA21_TOP | EM_DSXTA21_FA | N/A | N/A
|  | R_CS_SEL13 | from TA13 to TA23 | EM_DSXTA23_TOP | EM_DSXTA23_FA | N/A | N/A
|  | R_CS_SEL14 | from TA13 to TA30 | EM_DSXTA30_TOP | EM_DSXTA30_FA | N/A | N/A
|  | R_CS_SEL15 | from TA13 to SUBAG | N/A | N/A | N/A | N/A
| PH_X_TA12 | R_CS_SEL1 | from TA12 to TA26 | EM_DSXTA26_TOP | EM_DSXTA26_FA | N/A | BUF_TS_2
|  | R_CS_SEL2 | from TA12 to TA27 | EM_DSXTA27_TOP | EM_DSXTA27_FA | N/A | BUF_TS_2
|  | R_CS_SEL3 | from TA12 to TA28 | EM_DSXTA28_TOP | EM_DSXTA28_FA | N/A | BUF_TS_2
|  | R_CS_SEL4 | from TA12 to TA29 | EM_DSXTA29_TOP | EM_DSXTA29_FA | N/A | BUF_TS_2
|  | R_CS_SEL5 | from TA12 to TA31 | EM_DSXTA31_TOP | EM_DSXTA31_FA | N/A | BUF_TS_2
|  | R_CS_SEL6 | from TA12 to TA16 | EM_DSXTA16_TOP | EM_DSXTA16_FA | N/A | N/A
|  | R_CS_SEL7 | from TA12 to TA18 | EM_DSXTA18_TOP | EM_DSXTA18_FA | N/A | N/A
|  | R_CS_SEL8 | from TA12 to TA22 | EM_DSXTA22_TOP | EM_DSXTA22_FA | N/A | N/A
|  | R_CS_SEL9 | from TA12 to TA24 | EM_DSXTA24_TOP | EM_DSXTA24_FA | N/A | N/A
|  | R_CS_SEL10 | from TA12 to TA17 | EM_DSXTA17_TOP | EM_DSXTA17_FA | N/A | N/A
|  | R_CS_SEL11 | from TA12 to TA19 | EM_DSXTA19_TOP | EM_DSXTA19_FA | N/A | N/A
|  | R_CS_SEL12 | from TA12 to TA21 | EM_DSXTA21_TOP | EM_DSXTA21_FA | N/A | N/A
|  | R_CS_SEL13 | from TA12 to TA23 | EM_DSXTA23_TOP | EM_DSXTA23_FA | N/A | N/A
|  | R_CS_SEL14 | from TA12 to TA30 | EM_DSXTA30_TOP | EM_DSXTA30_FA | N/A | N/A
|  | R_CS_SEL15 | from TA12 to SUBAG | N/A | N/A | N/A | N/A

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_BH_LI_SP | YES | BH tank level setpoint | real | L | 5 | 0 | 100
| R_BP_PI_SP | YES | BP tank pressure control setpoint | real | barg | 1.5 | 0 | 3
| R_BP_PI_DEV_SP | NO | Deviation | real | barg | 0.1 | 0 | 1
| R_BH_PI_SP | YES | BH tank pressure control setpoint | real | barg | 0.5 | 0 | 3
| R_BH_PI_DEV_SP | NO | Deviation | real | barg | 0.1 | 0 | 1
| R_BP_WI_SP | YES | BP tank weight set point for buffer transfer | real | kg | 10 | 0 | 8000
| X_TA15_BH CS_SEL1 | YES | from TA15 to TA32 | N/A | N/A | N/A | N/A | N/A
| X_TA15_BH CS_SEL2 | YES | from TA15 to TA33 | N/A | N/A | N/A | N/A | N/A
| X_TA15_BH CS_SEL3 | YES | from TA15 to TA34 | N/A | N/A | N/A | N/A | N/A
| X_TA15_BH CS_SEL4 | YES | from TA15 to TA35 | N/A | N/A | N/A | N/A | N/A
| X_TA15_BH CS_SEL5 | YES | from TA15 to TA26 | N/A | N/A | N/A | N/A | N/A
| X_TA15_BH CS_SEL6 | YES | from TA15 to TA27 | N/A | N/A | N/A | N/A | N/A
| X_TA15_BH CS_SEL7 | YES | from TA15 to TA28 | N/A | N/A | N/A | N/A | N/A
| X_TA15_BH CS_SEL8 | YES | from TA15 to TA29 | N/A | N/A | N/A | N/A | N/A
| X_TA15_BH CS_SEL9 | YES | from TA15 to TA31 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL1 | YES | from TA14 to TA32 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL2 | YES | from TA14 to TA33 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL3 | YES | from TA14 to TA34 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL4 | YES | from TA14 to TA35 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL5 | YES | from TA14 to TA26 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL6 | YES | from TA14 to TA27 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL7 | YES | from TA14 to TA28 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL8 | YES | from TA14 to TA29 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL9 | YES | from TA14 to TA31 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL10 | YES | from TA14 to TA16 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL11 | YES | from TA14 to TA18 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL12 | YES | from TA14 to TA22 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL13 | YES | from TA14 to TA24 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL14 | YES | from TA14 to TA17 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL15 | YES | from TA14 to TA19 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL16 | YES | from TA14 to TA21 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL17 | YES | from TA14 to TA23 | N/A | N/A | N/A | N/A | N/A
| X_TA14_BH CS_SEL18 | YES | from TA14 to TA30 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL1 | YES | from TA13 to TA26 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL2 | YES | from TA13 to TA27 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL3 | YES | from TA13 to TA28 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL4 | YES | from TA13 to TA29 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL5 | YES | from TA13 to TA31 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL6 | YES | from TA13 to TA16 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL7 | YES | from TA13 to TA18 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL8 | YES | from TA13 to TA22 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL9 | YES | from TA13 to TA24 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL10 | YES | from TA13 to TA17 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL11 | YES | from TA13 to TA19 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL12 | YES | from TA13 to TA21 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL13 | YES | from TA13 to TA23 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL14 | YES | from TA13 to TA30 | N/A | N/A | N/A | N/A | N/A
| X_TA13_BH CS_SEL15 | YES | from TA13 to SUBAG | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL1 | YES | from TA12 to TA26 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL2 | YES | from TA12 to TA27 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL3 | YES | from TA12 to TA28 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL4 | YES | from TA12 to TA29 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL5 | YES | from TA12 to TA31 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL6 | YES | from TA12 to TA16 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL7 | YES | from TA12 to TA18 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL8 | YES | from TA12 to TA22 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL9 | YES | from TA12 to TA24 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL10 | YES | from TA12 to TA17 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL11 | YES | from TA12 to TA19 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL12 | YES | from TA12 to TA21 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL13 | YES | from TA12 to TA23 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL14 | YES | from TA12 to TA30 | N/A | N/A | N/A | N/A | N/A
| X_TA12_BH CS_SEL15 | YES | from TA12 to SUBAG | N/A | N/A | N/A | N/A | N/A
| R_MAX_TM_STEP1 | NO | Maximum step execution time for MESSAGE step, hold if exceed the time | int | min | 30 | 0 | 240
| R_MAX_TM_STEP2 | NO | Maximum step execution time for CHECK LEVEL step, hold if exceed the time | int | min | 30 | 0 | 240
| R_MAX_TM_STEP3 | NO | Maximum step execution time for PRES CONTROL step, hold if exceed the time | int | min | 30 | 0 | 240
| R_MAX_TM_STEP4 | NO | Maximum step execution time for BUF_X_BH step, hold if exceed the time | int | min | 240 | 0 | 600
| R_MAX_TM_STEP5 | NO | Maximum step execution time for BUF_X_SUBAG step, hold if exceed the time | int | min | 240 | 0 | 600
| R_TM_X_DELAY | NO | Delay timer for buffer transfer | real | sec | 30 | 0 | 600
| R_TM_FILT_DRN | NO | Delay timer for filter buffer drain | real | min | 2 | 0 | 60
| R_TM_VENT | NO | Delay timer to close after vent | real | sec | 60 | 0 | 600
| R_PT_RELEASE | YES | Set Point for Releasing Tank Pressure. | real | barg | 0.1 | 0 | 0.5
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase Pipe from The defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_BH_LIT_PV |  | BH tank LIT value recorded | real | L | N/A | N/A | N/A
| L_BH_PI_PV |  | BH tank PI value recorded | real | barg | N/A | N/A | N/A
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXBP01/E-DSXBH01 Emergency Stop
| Hold03 |  | BP&BH tank PIT fault
| Hold04 |  | BH tank LIT fault

## ALARM (hidden)
INDICATION | S150~S180