## Cover Sheet
Phase Specification PH_X_BH_DIS
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-001621 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_.....
| Step | max. 16 characters, _ for delimiter
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-25 | 杜林茂 | Draft
| 0.1a | 2020-10-28 | 杜林茂 | Updated based on comments
| 0.1b | 2020-11-10 | 杜林茂 | 1. Action Table： 将PH_X_TA33_DIS对应Note1的Command改为N/A; 更新S1010对应的Controller Settings描述 2. ParameterHold Tables： 更新参数命名
| 0.1c | 2020-11-20 | 杜林茂 | 1. SFC_HOLD_ABORT： 删除S7000和S8000 2. Action Table： 删除S7000和S8000及相关Command； 将HOLD的Command改为CLOSE 3. ParameterHold Tables: 增加路径选项参数
| 0.1d | 2020-12-10 | 杜林茂 | Action Table：删除EM_BH_POU和Note2
| 1.0 | 2021-03-03 | 杜林茂
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号
| 2.0b | 2021-06-05 | 王树深 | 更新急停策略
| 2.0c | 2021-06-22 | 王树深 | 增加上下游信号交互
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase X_BH_DIS is used for transferring buffer from Buffer Holding Tank to Buffer Distribution Valve.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| BH Tank | 3000L BUFFER HOLDING TANK UNIT TA16
3000L BUFFER HOLDING TANK UNIT TA17
3000L BUFFER HOLDING TANK UNIT TA18
3000L BUFFER HOLDING TANK UNIT TA19
3000L PROCESS WATER TANK UNIT TA20
3000L BUFFER HOLDING TANK UNIT TA21
3000L BUFFER HOLDING TANK UNIT TA22
3000L BUFFER HOLDING TANK UNIT TA23
3000L BUFFER HOLDING TANK UNIT TA24
6000L 0.1M NaOH TANK UNIT TA26
6000L BUFFER HOLDING TANK UNIT TA27
6000L BUFFER HOLDING TANK UNIT TA28
6000L BUFFER HOLDING TANK UNIT TA29
3000L BUFFER HOLDING TANK UNIT TA30
6000L BUFFER HOLDING TANK UNIT TA31
9000L 0.5M NaOH TANK UNIT TA32
9000L BUFFER HOLDING TANK UNIT TA33
9000L BUFFER HOLDING TANK UNIT TA34
9000L BUFFER HOLDING TANK UNIT TA35
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| BH Tank | EM_BH_BOM
EM_BH_FA
EM_BH_DIS

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
BH_PIT(Note1):
PIT_DSXTA3201A
PIT_DSXTA3201B
PIT_DSXTA3401A
PIT_DSXTA3401B
PIT_DSXTA2601A
PIT_DSXTA2601B
PIT_DSXTA2801A
PIT_DSXTA2801B
PIT_DSXTA3101A
PIT_DSXTA1601A
PIT_DSXTA1601B
PIT_DSXTA2201A
PIT_DSXTA2201B
PIT_DSXTA2001A
PIT_DSXTA1701A
PIT_DSXTA1701B
PIT_DSXTA2101A
PIT_DSXTA2101B
PIT_DSXTA3001A
Note: | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Step |  | Description | EM_BH_BOM | EM_BH_DIS | EM_BH_FA | Record Report | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A
S9010 | ERROR_MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查SPH_X_TATE是否正确 Check if the SPH_X_TATE is correct or not | N/A | N/A | N/A
S9030 | ERROR_MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A
S9050 | ERROR_MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A
S1010 | BUFFER_SUP | 缓冲液转移到用点 Buffer supply to point of use | PD_OUT | Note 1 | PRESSURE_CONT |  |  | EM_BH_FA: SP=R_BH_PI_SP △P=R_BH_PI_DEV_SP
S1020 | MSG | 提示是否结束转料 Prompt to stop buffer transfer | PD_OUT | Note 1 | PRESSURE_CONT |  |  | EM_BH_FA: SP=R_BH_PI_SP △P=R_BH_PI_DEV_SP
S1030 | SET_STATE | 设置状态 Set state | CLOSE | CLOSE | PRESSURE_CONT |  |  | EM_BH_FA: SP=R_BH_PI_SP △P=R_BH_PI_DEV_SP | Source Tank = Dirty Line State = Dirty
S2010 | INTERACTION | 等待交互信号 Waitting for Interaction Single. | N/A | N/A | N/A
S2020 | BUFFER_SUP1 | 缓冲液加压转移到用点 Buffer supply to point of use with pressure. | PD_OUT | N/A | PRESSURE_CONT |  |  | EM_BH_FA: SP=R_BH_PI_SP2 △P=R_BH_PI_DEV_SP2 | Send DSX_PD_Trans_Red=1
S2030 | BUFFER_SUP2 | 缓冲液转不带压移到用点 Buffer supply to point of use without Pressure. | PD_OUT | N/A | PRESSURE_CONT |  |  | EM_BH_FA: SP=R_BH_PI_SP3 △P=R_BH_PI_DEV_SP3
S3010 | INTERACTION | 等待交互信号 Waitting for Interaction Single. | N/A | N/A | N/A
S3020 | BUFFER_SUP3 | 缓冲液加压转移到用点 Buffer supply to point of use with pressure. | PD_OUT | N/A | PRESSURE_CONT |  |  | EM_BH_FA: SP=R_BH_PI_SP4 △P=R_BH_PI_DEV_SP4 | Send DSX_BU_Trans_Red=1
S7010 | HOLD | 暂停 pause | CLOSE | CLOSE | CLOSE
S8010 | ABORT | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE
S8020 | SET_STATE | 设置状态 Set state | CLOSE | CLOSE | CLOSE |  |  |  | Source Tank = Process Line State = Process
|  | Phase | EM_BH_BOM | EM_BH_DIS (Note1) | EM_BH_FA
|  | R_X_TA16_DIS_SEL | EM_DSXTA16_BOM | N/A | EM_DSXTA16_FA
|  | R_X_TA33_DIS_SEL | EM_DSXTA33_BOM | N/A | EM_DSXTA33_FA
|  | R_X_TA21_DIS_SEL | EM_DSXTA21_BOM | N/A | EM_DSXTA21_FA
|  | R_X_TA34_DIS_SEL | EM_DSXTA34_BOM | TA34 _TO_ CHT01_02 | EM_DSXTA34_FA
|  | R_X_TA22_DIS_SEL | EM_DSXTA22_BOM | N/A | EM_DSXTA22_FA
|  | R_X_TA29_DIS_SEL | EM_DSXTA29_BOM | N/A | EM_DSXTA29_FA
|  | R_X_TA35_DIS_SEL | EM_DSXTA35_BOM | N/A | EM_DSXTA35_FA
|  | R_X_TA24_DIS_SEL | EM_DSXTA24_BOM | N/A | EM_DSXTA24_FA
|  | R_X_TA30_DIS_SEL | EM_DSXTA30_BOM | TA30 _TO_ TA06UF02 | EM_DSXTA30_FA
|  | R_X_TA32_DIS_SEL | EM_DSXTA32_BOM | N/A | EM_DSXTA32_FA
|  | R_X_TA26_DIS_SEL | EM_DSXTA26_BOM | N/A | EM_DSXTA26_FA
|  | R_X_TA20_DIS_SEL | EM_DSXTA20_BOM | N/A | EM_DSXTA20_FA
|  | R_X_TA17_DIS_SEL | EM_DSXTA17_BOM | N/A | EM_DSXTA17_FA
|  | R_X_TA19_DIS_SEL | EM_DSXTA19_BOM | N/A | EM_DSXTA19_FA
|  | R_X_TA23_DIS_SEL | EM_DSXTA23_BOM | N/A | EM_DSXTA23_FA
|  | R_X_TA18_DIS_SEL | EM_DSXTA18_BOM | N/A | EM_DSXTA18_FA
|  | R_X_TA27_DIS_SEL | EM_DSXTA27_BOM | N/A | EM_DSXTA27_FA
|  | R_X_TA28_DIS_SEL | EM_DSXTA28_BOM | N/A | EM_DSXTA28_FA
|  | R_X_TA31_DIS_SEL | EM_DSXTA31_BOM | N/A | EM_DSXTA31_FA
"X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max | REV.2a
| R_SEL | NO | SEL1:PD Transfer to Precess Parts. | Name Set | N/A | 1 | 0 | 99
|  |  | SEL2:PD Transfer for Havest. | Name Set | N/A | 2 | 0 | 99
|  |  | SEL3:PD Transfer for Flush CF. | Name Set | N/A | 3 | 0 | 99
| R_X_TA16_DIS_SEL | YES | Buffer transfer from TA16 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA33_DIS_SEL | YES | Buffer transfer from TA33 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA21_DIS_SEL | YES | Buffer transfer from TA21 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA34_DIS_SEL | YES | Buffer transfer from TA34 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA22_DIS_SEL | YES | Buffer transfer from TA22 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA29_DIS_SEL | YES | Buffer transfer from TA29 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA35_DIS_SEL | YES | Buffer transfer from TA35 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA24_DIS_SEL | YES | Buffer transfer from TA24 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA30_DIS_SEL | YES | Buffer transfer from TA30 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA32_DIS_SEL | YES | Buffer transfer from TA32 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA26_DIS_SEL | YES | Buffer transfer from TA26 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA20_DIS_SEL | YES | Buffer transfer from TA20 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA17_DIS_SEL | YES | Buffer transfer from TA17 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA19_DIS_SEL | YES | Buffer transfer from TA19 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA23_DIS_SEL | YES | Buffer transfer from TA23 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA18_DIS_SEL | YES | Buffer transfer from TA18 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA27_DIS_SEL | YES | Buffer transfer from TA27 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA28_DIS_SEL | YES | Buffer transfer from TA28 to distribution | N/A | N/A | N/A | N/A | N/A
| R_X_TA31_DIS_SEL | YES | Buffer transfer from TA31 to distribution | N/A | N/A | N/A | N/A | N/A
| R_BH_PI_SP | YES | BH tank pressure control set point | real | barg | 0.5 | 0 | 3
| R_BH_PI_DEV_SP | NO | Deviation | real | barg | 0.2 | 0 | 1
| R_BH_PI_SP2 | YES | Set Point for Buffer supply to point of use with Pressure. | real | barg | 1 | 0 | 3
| R_BH_PI_DEV_SP2 | NO | Deviation | real | barg | 0.2 | 0 | 1
| R_BH_PI_SP3 | YES | Set Point for Buffer supply to point of use without Pressure. | real | barg | 0.1 | 0 | 3
| R_BH_PI_DEV_SP3 | NO | Deviation | real | barg | 0.02 | 0 | 1
| R_BH_PI_SP4 | YES | Set Point for Buffer supply to point of use with pressure. | real | barg | 0.1 | 0 | 3
| R_BH_PI_DEV_SP4 | NO | Deviation | real | barg | 0.02 | 0 | 1
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | BH tank LIT low level
| Hold03 |  | DSX_PD_Alarm_Rcv=1 or DSX_PD_Alarm_Snd=1 ; DSX_BU_Alarm_Rcv=1 or DSX_BU_Alarm_Snd=1.
| Hold04 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR06/E-DSXPUR07 Emergency Stop
Q

## ALARM (hidden)
INDICATION | S150~S180