## Cover Sheet
Phase Specification PH_X_BH_VF
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-001632 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
2.0b
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-25 | 刘会莹 | Draft
| 0.1a | 2020-10-29 | 刘会莹 | Update according to comments
| 0.1b | 2020-11-09 | 刘会莹 | Update according to comments
| 0.1c | 2020-11-20 | 刘会莹 | 修改Stop数控图，删除stop步骤
| 0.1d | 2020-12-10 | 杜林茂 | 1. Description 删除Unit Class中不相关项 2. Action Table 更新S1020~1050中EM_VF01_IN_DIS对应Command; 增加EM_BH_POU
| 1.0 | 2021-03-03 | 杜林茂 | 根据程序仿真更新
| 2.0 | 2021-04-12 | 杜林茂 | 增加急停编号
| 2.0a | 2021-05-17 | 王树深 | Action table 更新command
| 2.0b | 2021-06-05 | 王树深 | 更新急停策略
| 2.0c | 2021-06-09 | 王树深 | 冲洗过滤器时泵速改为用流量控制
| 2.0d | 2021-07-13 | 王树深 | S2030步中EM_VF01_FILT的command改为PE_CIP；S1040步流量控制改成泵速控制
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase PH_X_BH_VF is used for transferring buffer from Buffer holding tank to VF.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class |  | Units |  |  |  | 2.0b
| Process Equipment （无需信号交互） |  | NF WORK UNIT NF01 | UF0301
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
| EM's at own Unit |  |  |  |  | 2021-06-05
| Unit |  | Equiment Module |  |  | 2021-06-05
| NF WORK UNIT NF01 | UF0301 | EM_DF04 | EM_VF01_IN_DIS | EM_VF01_FILT
| 3000L PURIFICATION TANK UNIT TA08 |  | EM_PUR_TOP | EM_PUR_FA1 | EM_BH_POU

## SFC_CHECK
8. | SFC Check Steps for RUN Logic
2.0b
2021-06-05
2021-06-05

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN
8. | RUN Logic without Check Steps
2.0b
2021-06-05
2021-06-05

## SFC_HOLD_ABORT_STOP
8. | HOLD and ABORT Logic
2.0b
2021-06-05
2021-06-05

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
|  | Phase | EM
|  | Phase: TA30_TO_NF01 CS_SEL1:Pre-filter flush | EM_DSXDF04 | EM_DSXVF01IN_DIS | EM_FDSXVF0101 | N/A | N/A | N/A
|  | Phase: TA30_TO_NF01 CS_SEL 2:VF-filter flush | EM_DSXDF04 | EM_DSXVF01IN_DIS | EM_FDSXVF0101 | EM_DSXTA08_TOP | N/A | N/A
|  | Phase: TA30_TO_NF01 CS_SEL 3:PD_Recovery | EM_DSXDF04 | EM_DSXVF01IN_DIS | EM_FDSXVF0101 | EM_DSXTA08_TOP | EM_DSXTA08_FA | N/A
|  | Phase: TA20_TO_NF01 CS_SEL1:Pre-filter flush | EM_DSXDF04 | EM_DSXVF01IN_DIS | EM_FDSXVF0101 | N/A | N/A | EM_DSXTA20_VF01
|  | Phase: TA20_TO_NF01 CS_SEL 2:VF-filter flush | EM_DSXDF04 | EM_DSXVF01IN_DIS | EM_FDSXVF0101 | EM_DSXTA08_TOP | N/A | EM_DSXTA20_VF01 |  |  |  |  | 2.0b
|  | Phase: TA20_TO_NF01 CS_SEL 3:PD_Recovery | EM_DSXDF04 | EM_DSXVF01IN_DIS | EM_FDSXVF0101 | EM_DSXTA08_TOP | EM_DSXTA08_FA | EM_DSXTA20_VF01
Step |  | Description | EM_DF04 | EM_VF01_IN_DIS | EM_VF01_FILT | EM_PUR_TOP | EM_PUR_FA1 | EM_BH_POU | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | 2021-06-05 | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | 2021-06-05 | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | MSG | 提示过滤准备就绪，连接软管。准备完成后确认。 Operator message: VF ready, hose connected ? | N/A | N/A | N/A | N/A | N/A | N/A
S1020 | PU_PRE | 延时以灌泵 Time delay for pump fill. | Note1 | PD_TO_PU | DF_PRE_RINSE | N/A | N/A | BUF_OUT | If PIT-DSXNF0101＞R_PT1_ALM，hold； If PIT-DSXNF0102＞R_PT1_ALM，hold； If PIT-DSXNF0103＞R_PT1_ALM，hold； If PIT-DSXNF0104＞R_PT1_ALM，hold； If PIT-DSXNF0101-PIT-DSXNF0102 >R_DP1_ALM, hold； If PIT-DSXNF0102-PIT-DSXNF0103 >R_DP2_ALM, hold；
S1030 | MSG | 延时以使过滤器排气 Time delay for filter vent. | Note3 | PD_TO_PU | DF_PRE_RINSE | N/A | N/A | BUF_OUT |  |  |  | 固定泵速
S1040 | BUF_SUP | 缓冲液转移到用点 Buffer supply to point of use | Note3 | PD_TO_PU | DF_PRE_RINSE | N/A | N/A | BUF_OUT |  | Adjust flow through PID |  | 固定泵速
S1050 | PU_STOP | 延时以停泵 Time delay for pump stop | Note1 | PD_TO_PU | DF_PRE_RINSE | N/A | N/A | BUF_OUT |  |  |  | 只通过流量调节控制阀开度
S1060 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | N/A | N/A | CLOSE
S1070 | SET_STATE | 状态变更 Set State | CLOSE | CLOSE | CLOSE | N/A | N/A | CLOSE |  |  | Line State = Dirty or Process
S2010 | MSG | 提示过滤准备就绪，连接软管。准备完成后确认。 Operator message:VF ready, hose connected ? | N/A | N/A | N/A | N/A | N/A | N/A
S2020 | PU_PRE | 延时以灌泵 Time delay for pump fill. | Note1 | PD_TO_PU | NF_PRE_RINSE | PD_IN_DRN1 | N/A | BUF_OUT | If PIT-DSXNF0101＞R_PT1_ALM，hold； If PIT-DSXNF0102＞R_PT1_ALM，hold； If PIT-DSXNF0103＞R_PT1_ALM，hold； If PIT-DSXNF0104＞R_PT1_ALM，hold； If PIT-DSXNF0101-PIT-DSXNF0102 >R_DP1_ALM, hold； If PIT-DSXNF0102-PIT-DSXNF0103 >R_DP2_ALM, hold；
S2021 | MSG | 延时以使过滤器排气 Time delay for filter vent. | Note3 | PD_TO_PU | NF_PRE_RINSE | N/A | N/A | BUF_OUT |  |  |  | 固定泵速
S2030 | VENT | 延时以使过滤器排气 Time delay for filter vent. | Note3 | PD_TO_PU | PE_CIP | PD_IN_DRN1 | N/A | BUF_OUT |  |  |  | 固定泵速
S2040 | BUF_SUP | 缓冲液转移到用点 Buffer supply to point of use | Note2 | PD_TO_PU | PD_TS1 | PD_IN_DRN1 | N/A | BUF_OUT |  | Adjust DP2 through PID |  | 只通过流量调节控制阀开度
S2050 | PU_STOP | 延时以停泵 Time delay for pump stop | Note1 | PD_TO_PU | PD_TS1 | PD_IN_DRN1 | N/A | BUF_OUT |  |  |  | 只通过流量调节控制阀开度
S2060 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | N/A | CLOSE
S2070 | SET_STATE | 状态变更 Set State | CLOSE | CLOSE | CLOSE | CLOSE | N/A | CLOSE |  |  | Line State = Dirty or Process
S3010 | MSG | 提示过滤准备就绪，连接软管。准备完成后确认。 Operator message: VF ready, hose connected ? | N/A | N/A | N/A | N/A | N/A | N/A
S3020 | PU_PRE | 延时以灌泵 Time delay for pump fill. | Note1 | PD_TO_PU | PD_TS1 | PD_IN | VENT_FA | BUF_OUT | If PIT-DSXNF0101＞R_PT1_ALM，hold； If PIT-DSXNF0102＞R_PT1_ALM，hold； If PIT-DSXNF0103＞R_PT1_ALM，hold； If PIT-DSXNF0104＞R_PT1_ALM，hold； If PIT-DSXNF0101-PIT-DSXNF0102 >R_DP1_ALM, hold； If PIT-DSXNF0102-PIT-DSXNF0103 >R_DP2_ALM, hold； | EM_PUR_FA1: SP1=R_PT_SP1 △P1=R_PT_SP1_DEV
S3040 | BUF_SUP | 缓冲液转移到用点 Buffer supply to point of use | Note2 | PD_TO_PU | PD_TS1 | PD_IN | VENT_FA | BUF_OUT |  | EM_PUR_FA1: SP1=R_PT_SP1 △P1=R_PT_SP1_DEV Adjust DP2 through PID |  | 只通过流量调节控制阀开度
S3050 | PU_STOP | 延时以停泵 Time delay for pump stop | Note1 | PD_TO_PU | PD_TS1 | PD_IN | VENT_FA | BUF_OUT |  | EM_PUR_FA1: SP1=R_PT_SP1 △P1=R_PT_SP1_DEV |  | 只通过流量调节控制阀开度
S3060 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | VENT_FA | CLOSE |  | EM_PUR_FA1: SP1=R_PT_SP1 △P1=R_PT_SP1_DEV
S3070 | SET_STATE | 状态变更 Set State | CLOSE | CLOSE | CLOSE | CLOSE | PRESSURE_CONT | CLOSE |  | EM_PUR_FA1: SP1=R_PT_SP1 △P1=R_PT_SP1_DEV | Target Tank = Process Line State = Dirty or Process
S7010 | HOLD | 暂停pause | HOLD | CLOSE | HOLD | HOLD | HOLD | HOLD
S8010 | ABORT | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S8020 | SET_STATE | 状态变更 Set State | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Target Tank = Process Line State = Process
|  |  | Note1 | Note4 | Note2 | Note3
|  | Phase: TA30_TO_NF01 | BUF_FR_TA30 | BUF_FR_TA30_FC | BUF_FR_TA30_PU | BUF_FR_TA30_SPD
|  | Phase: TA20_TO_NF01 | WFI_FR_TA20 | WFI_FR_TA20_FC | WFI_FR_TA20_PU | WFI_FR_TA20_SPD

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_PT_SP2 | Yes | Process Tank TA08 pressure set point | real | barg | 0.5 | 0 | 2
| R_PT_SP2_DEV | NO | Process Tank TA08 pressure Deviation | real | barg | 0.2 | 0 | 1
| R_BH_VF_X_SEL | YES | Supply buffer from TA30 to VF | Name set | N/A | TA30_TO_NF01 | N/A | N/A
|  | YES | Supply buffer from TA20 to VF |  | N/A | TA20_TO_NF01 | N/A | N/A | 2.0b
| R_CS_SEL | YES | Supply buffer for Pre-filter flush | Name set | N/A | Pre_Filter_Flush | 0 | 99
|  | YES | Supply buffer for VF-filter flush |  | N/A | VF_Filter_Flush | 0 | 99
|  | YES | Supply buffer for PD_Recovery |  | N/A | PD_Recovery | 0 | 99
| R_PU_PRE_TM | NO | Time delay for pump fill. | Real | min | 5 | 0 | 60
| R_VENT_TM | NO | Time delay for vent. | Real | min | 5 | 0 | 60
| R_PU_SPD_LL | YES | Fixed pump speed for vent | Real | rpm | 500 | 0 | 2500
| R_DPIC_SP | YES | PIT-DSXNF0102- PIT-DSXNF0103 set point | Real | psi | 26 | 0 | 70
| R_FQ_SP | YES | Buffer quantity for flush. | Real | kg | 200 | 0 | 9999
| R_PU_STOP_TM | NO | Time delay for pump stop. | Int | sec | 30 | 0 | 300
| R_FIC_SP | YES | Flowrate set point | Real | L/h | 1000 | 0 | 6500
| R_PT1_ALM | NO | VF PI01 pressure for alarm | Real | barg | 4 | 0 | 5
| R_PT2_ALM | NO | VF PI02 pressure for alarm | Real | barg | 4 | 0 | 5
| R_PT3_ALM | NO | VF PI03 pressure for alarm | Real | barg | 4 | 0 | 5
| R_PT4_ALM | NO | VF PI04 pressure for alarm | Real | barg | 4 | 0 | 5
| R_DP1_ALM | YES | Pre-filter Differential pressure for alarm | Real | barg | 3 | 0 | 5
| R_DP2_ALM | YES | VF Differential pressure for alarm | Real | barg | 4 | 0 | 5
| R_FCV_SP | YES | Set point of control vavle opening | Real | % | 100 | 0 | 100
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Eng.Unit | Step | Begin | End
| L_FQ_PV |  | Buffer quantity for flush. | kg
| L_PT1_PV |  | Pressure value for PIT-DSXNF0101 | barg
| L_PT2_PV |  | Pressure value for PIT-DSXNF0102 | barg
| L_PT3_PV |  | Pressure value for PIT-DSXNF0103 | barg
| L_PT4_PV |  | Pressure value for PIT-DSXNF0104 | barg
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/ E-DSXPUR02/ E-DSXPUR03/ E-DSXPUR04/ E-DSXPUR06/ E-DSXPUR07 Emergency Stop
| Hold04 |  | PT_DSXNF0101 fault
| Hold05 |  | PT_DSXNF0102 fault
| Hold06 |  | PT_DSXNF0104 fault
| Hold07 |  | PT_DSXNF0103 fault

## ALARM (hidden)
INDICATION | S150~S180