## Cover Sheet
Phase Specification
PH_TA20_WFI_IN
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004271 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-11-06 | 杜林茂 | Draft
0.1
0.2
0.3
| 0.1a | 2020-11-20 | 杜林茂 | hold abort命令更新
| 1.0 | 2021-03-03 | 杜林茂 | 1.SFC_RUN: 增加自动补水，自动排放和加水温度判断逻辑； 增加非自结束选项 2. Action Table：根据顺控图更新 3. ParameterHold Tables：更新INPUT和REPORT参数 4. 根据FAT修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号
| 2.0b | 2021-07-06 | 王树深 | 更新TA20注水供水取样逻辑
| 2.0c | 2021-07-14 | 王树深 | 更新TA20注水供水取样逻辑
| 2.0d | 2021-07-21 | 王树深 | 更新command
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase TA20_WFI_IN is used for adding WFI into tank. 1. DCS will control the POU valve which supplied and installed by CU system.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Buffer Holding Tank | 3000L PROCESS WATER TANK UNIT TA20 | DS1-TA12
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Buffer Holiding Tank | EM_TA20_HEX
EM_BP_TOP
EM_BH_FA
EM_BH_BOM
EM_BH_DIS_DRN_A
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| N/A | N/A

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase | EM
Buffer Holding Tank |  | DSXTA20_WFI_IN | EM_DSXTA20_HEX | EM_DSXTA20_TOP | EM_DSXTA20_FA | EM_DSXTA20_BOM | EM_DSXTA20DISDRN
Step |  | Description | EM_TA20_HEX | EM_BP_TOP | EM_BH_FA | EM_BH_BOM | EM_BH_DIS_DRN_A | Alarm Settings | Controller Settings | Other Actions | REV.2 | 删除EM
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A
S1000 | CHECK_TEMP | 换热器后温度判断 Temperature check after heat exchanger | TEMP_EXCHANGE | WFI_FLUSH_DRN | CLOSE | CLOSE | CLOSE |  | EM_DSXTA20_HEX: SP=R_TI_SP ΔP=R_TI_SP_DEV
S1010 | PIPE_EXHAUST | 输送管道排气 Exhausting of transfer pipe | TEMP_EXCHANGE | WFI_IN_TA20 | VENT_FA | PD_OUT | PE_DRN |  | EM_DSXTA20_HEX: SP=R_TI_SP ΔP=R_TI_SP_DEV
S1020 | WFI_IN | 罐中WFI加注 Add WFI in tank | TEMP_EXCHANGE | WFI_IN_TA20 | PRESSURE_CONT | PD_PUT | CLOSE |  | Enable LEVEL-CONTROL commands force If LIT-DSXTA2001< R_LI_LOW_SP, start S1020, Still LIT-DSXTA2001>= R_LI_HIGH_SP.Then close S1020, start S1030,S1040. EM_DSXTA20_TOP: SP=R_TI_SP ΔT=R_TI_SP_DEV EM_DSXTA20_TOP: SP=R_PI_SP ΔP=R_PI_SP_DEV | Start R_MAX_TM_WFI_IN at start of S1020
S1030 | BLOW_WFI | 压空吹扫WFI进罐 Air blow the WFI into the tank | BLOW_WFI_IN_TK | WFI_DEL_CLO | PRESSURE_CONT | PD_PUT | CLOSE |  | EM_DSXTA20_TOP: SP=R_PI_SP ΔP=R_PI_SP_DEV
S1040 | BLOW_HEX | 压空吹排换热器残余WFI PA exhausting residual WFI of heat exchanger | BLOW_HEX | WFI_DRN | PRESSURE_CONT | PD_PUT | CLOSE |  | EM_DSXTA20_TOP: SP=R_PI_SP ΔP=R_PI_SP_DEV
S1050 | MESSAGE | 提示选择排放或者取样 Prompt to choose drain or sample | CLOSE | CLOSE | PRESSURE_CONT | PD_PUT | CLOSE |  | EM_DSXTA20_TOP: SP=R_PI_SP ΔP=R_PI_SP_DEV
S1060 | DRAIN | 排空罐 Drain the tank | CLOSE | CLOSE | PRESSURE_CONT | PD_PUT | PE_DRN |  | Disable LEVEL-CONTROL commands force EM_DSXTA20_TOP: SP=R_PI_SP2 ΔP=R_PI_SP_DEV | Start R_MAX_TM_DRAIN at start of S1060
S1070 | FLUSH_TK | 冲洗罐子 Flush Tank | CLOSE | WFI_SPRAY | VENT_FA | PD_PUT | PE_DRN
S1080 | DR_DELAY | 排空延时 Delay drain | CLOSE | CLOSE | PRESSURE_CONT | PD_PUT | PE_DRN
S1090 | MESSAGE | 提示是否结束Phsae Prompt if to end the phase | CLOSE | CLOSE | VENT_FA | PD_PUT | PE_DRN
S1100 | CLOSE | 结束 CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S1110 | SET_STATE | 设置状态 Set the state | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Target Tank = DIRTY Line State = DIRTY
S1200 | CHECK_TEMP | 换热器后温度判断 Temperature check after heat exchanger | TEMP_EXCHANGE | WFI_FLUSH_DRN | PRESSURE_CONT | PD_PUT | CLOSE |  | EM_DSXTA20_HEX: SP=R_TI_SP ΔP=R_TI_SP_DEV EM_DSXTA20_TOP: SP=R_PI_SP ΔP=R_PI_SP_DEV
S1210 | FLUSH_PE | 冲洗WFI管道 Flush WFI-IN Pipe | TEMP_EXCHANGE | WFI_FLUSH_PE | PRESSURE_CONT | PD_PUT | CLOSE |  | EM_DSXTA20_HEX: SP=R_TI_SP ΔP=R_TI_SP_DEV EM_DSXTA20_TOP: SP=R_PI_SP ΔP=R_PI_SP_DEV
S1220 | MESSAGE | 提示是否开始取样 Prompt if to start smapling | TEMP_EXCHANGE | WFI_FLUSH_PE | PRESSURE_CONT | PD_PUT | CLOSE |  | EM_DSXTA20_HEX: SP=R_TI_SP ΔP=R_TI_SP_DEV EM_DSXTA20_TOP: SP=R_PI_SP ΔP=R_PI_SP_DEV
S1230 | WFI_SAMPLE | WFI取样 WFI Sampling | TEMP_EXCHANGE | WFI_FLUSH_PE | PRESSURE_CONT | PD_PUT | CLOSE |  | EM_DSXTA20_HEX: SP=R_TI_SP ΔP=R_TI_SP_DEV EM_DSXTA20_TOP: SP=R_PI_SP ΔP=R_PI_SP_DEV
S1240 | PE_DRN | WFI-IN管道排放 WFI-IN Pipe Drain | BLOW_HEX | WFI_DRN | PRESSURE_CONT | PD_PUT | CLOSE |  | EM_DSXTA20_TOP: SP=R_PI_SP ΔP=R_PI_SP_DEV
S7010 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD | HOLD | HOLD
S8010 | ABORT | 终止 Abort | ABORT | ABORT | ABORT | ABORT | ABORT
S8020 | SET_STATE | 设置状态 Set the state | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Target Tank = DIRTY Line State = DIRTY

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_TI_SP | YES | Temperature setpoint of WFI tank after heat exchanger | real | °C | 22.5 | 0 | 100
| R_TI_SP_DEV | NO | Deviation | real | °C | 2.5 | 0 | 10
| R_TM_PIPE_EXHAUST | YES | Time for Transfer pipe exhausting | real | min | 3 | 0 | 10
| R_PI_SP | YES | Tank pressure control setpoint for process | real | barg | 0.2 | 0 | 2
| R_PI_SP_DEV | NO | Deviation | real | barg | 0.1 | 0 | 1
| R_LI_HIGH_SP | YES | Required level setpoint of WFI adding | real | L | 2500 | 0 | 3000
| R_LI_LOW_SP | YES | Low level setpoint of WFI in tank | real | L | 1500 | 0 | 3000
| R_BLOW_WFI_TM | YES | Time for blowing WFI in tank by PA | real | min | 1 | 0 | 10
| R_BLOW_HEX_TM | YES | Time for blowing Heat Exchanger by PA | real | min | 3 | 0 | 10
| R_MAX_TM_WFI_IN | YES | Time limit for WFI injectioning in the tank | real | min | 300 | 0 | 500
| R_MAX_TM_Drain | YES | Time limit for draining tank | real | min | 120 | 0 | 300
| R_LI_EMPTY | YES | Level setpoint of draining tank empty | real | L | 20 | 0 | 1000
| R_TM_FLUSH_TK | YES | Time for Flushing Tank | real | min | 5 | 0 | 30
| R_TM_DR_DELAY | YES | Time for blowing Heat Exchanger by PA | real | min | 2 | 0 | 20
| R_TM_FLUSH_PE | YES | Time for Flushing WFI-IN Pipe | real | min | 5 | 0 | 30
| R_TM_SAMPLE | YES | WFI line sample time | real | min | 5 | 0 | 10
| R_TM_PE_DRN | YES | WFI line drain time | real | min | 2 | 0 | 10
| R_PI_SP2 | YES | Tank pressure control setpoint for tank drain | real | barg | 1 | 0 | 2
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
.
| Parameter |  | Description | Type | Eng. Unit | Step | Begin | End
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXBH01 Emergency Stop
| Hold03 |  | LIT/TIT/PIT fault
| Hold04 |  | R_MAX_TM_WFI_IN elapsed
| Hold05 |  | R_MAX_TM_Drain elapsed

## ALARM (hidden)
INDICATION | S150~S180