## Cover Sheet
Phase Specification PH_C_WT
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | 信达M2 FS_CIPstation_PH_C_WT |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张旭 | 2021-07-30 |  | 张旭
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-09-21 | Zhang Yuran | Draft for review
| 0.1 | 2020-11-27 | Zhang Yuran | Update for programming
| 1 | 2021-03-03 | Zhang Yuran | Update after SFAT
| 2.0b | 2021-06-03 | 王树深 | 增加罐子清洗后泵排和重力排
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase PH_C_WT is used for wash tank selfclean.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| CIP Station | DS1CIP02
DS1CIP03
DS1CIP05
DS2CIP02
DS2CIP03
DS2CIP05
DS3CIP02
DS3CIP03
DS3CIP05
DS4CIP02
DS4CIP03
DS4CIP05
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
EM_C_CIP
EM_C_BTH
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN（PH_C_WT)
8. | RUN Logic with Check Steps

## SFC_HOLD_ABORT_STOP
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Step |  | Description | TAG1 | TAG2 | TAG3 |  | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | TAG11 | TAG12 | TAG13 | TAG14 | TAG15 | TAG16 | TAG17 | TAG18 | TAG19 | TAG20 | TAG21 | TAG22 | TAG23 | TAG24 | TAG25 | TAG26 | TAG27 | TAG28 | TAG29 |  | TAG30 | TAG31 | TAG32 | TAG33 | Actions
|  |  | PU01 | PU02 | SIC001 PU03 |  | PV05 | PV08 | PV12 | PV15 | PV16 | PV17 | PV18 | PV19 | PV20 | PV21 | PV22 | PV23 | PV25 | PV26 | PV30 | PV31 | PV36 | PV37 | PV40 | PV41 | PV45 | PV46 | PV51 | PV52 | PV53 | TE02 TCV01 |  | PVALK | PW_REQ | WFI_REQ | EM_C_BTH
S9000 | EM_CHECK | EM检查 Check related EM | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Acquire EM_C_CIP&EM_C_BTH Transfer all parameters to EM_C_CIP
S9010 | ERROR_MESSAGE_1 | EM检查错误信息 EM check error message | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | MSG0: EM Status Check Failed, Please Select Continue (Yes) or Complete the Phase (No)
S9020 | STATE_CHECK | 状态检查 State check | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_MESSAGE_2 | 状态检查错误信息 State check error message | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | MSG0: Tank and Line Status Check Failed, Please Select Continue (Yes) or Complete the Phase (No)
S9040 | ROUTE_CHECK | 路经检查 Check related route | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_MESSAGE_3 | 路经检查错误信息 Route check error message | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | MSG0: Route Check Failed, Please Select Continue (Yes) or Complete the Phase (No)
S9060 | ENABLE_HM&SM | 使能报警 Enable phase related HM&SM | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S0100 | LEVEL_CHK | 确认罐子状态 check tank state | 0 | 0 | SP=0 | stop | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0% | 0 | 0 | 0 | STOP | MSG0: Check tank state level. A1: Set WT_WASH_TIMES = 0
T0200 | LIT01>=R_WT_LE_L
T0200-2 | R_CYC_WASH_TM elapsed
S0200 | PUMP_DRAIN | 泵抽水排放 Drain tank by pump | 0 | 0 | SP1 | A1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0% | 0 | 0 | 0 | WT_FILTER_OPEN | MSG0: Pump drain MSG1: Wait tank level LIT01<R_WT_LE_L A1: If PU03 is not running, SP1=R_PU_DRN_SPD, Delay R_PU_DELAY_TM, Then Start PU03. Else if PU03 is running, no more action, keep running.
T0300-1 | LIT01<R_WT_LE_L
S0300 | DRAIN_GRAVITY | 罐子重力自排 Drain tank by gravity | 0 | 0 | SP=0 | stop | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A1 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0% | 0 | 0 | 0 | WT_FILTER_OPEN | MSG0: Gravity drain MSG1: Wait R_DRN_ELAP_TM elasped A1:Open R_VLV_DELAY_TM ,then close
T0400 | R_DRN_ELAP_TM elapsed and WT_WASH_TIMES<R_WT_TIMES_SP
S0400 | SELF_WASH | 罐子自清洗 Tank selfwash and drain | 0 | 0 | SP=0 | stop | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | A3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0% | 0 | A1 | [ | WT_FILTER_OPEN | MSG0: Tank self wash and drain MSG1: Wait R_SELF_WASH_TM elasped A1: Send DSX_PW_REQ = 1.When PW is ready, start timer R_SELF_WASH_TM A2(R_SELF_WASH_TM complete): Send DSX_PW_REQ = 0. A3: pulse open R_VLV_PULSE_TM.
T0410 | R_SELF_WASH_TM elapsed
S0410 | PUMP_DRAIN | 泵抽水排放 Drain tank by pump | 0 | 0 | SP1 | A1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0% | 0 | 0 | 0 | WT_FILTER_OPEN | MSG0: Pump drain MSG1: Wait tank level LIT01<R_WT_LE_L A1: If PU03 is not running, SP1=R_PU_DRN_SPD, Delay R_PU_DELAY_TM, Then Start PU03. Else if PU03 is running, no more action, keep running.
T0420 | LIT01<R_WT_LE_L
S0420 | DRAIN_GRAVITY | 罐子重力自排 Drain tank by gravity | 0 | 0 | SP=0 | stop | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A1 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0% | 0 | 0 | 0 | WT_FILTER_OPEN | MSG0: Gravity drain MSG1: Wait R_DRN_ELAP_TM elasped A1:Open R_VLV_DELAY_TM ,then close
T0500 | R_DRN_ELAP_TM elapsed and WT_WASH_TIMES<R_WT_TIMES_SP
S0500 | PUMP_CYCLE | 自循环清洗 Tank selfwash with pump cycle | 0 | 0 | SP1 | A3 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | NA | 0% | 0 | A2 | 0 | WT_FILTER_OPEN | MSG0: Tank selfwash with pump cycle MSG1: Wait R_CYC_WASH_TM elasped A1: Send DSX_PW_REQ = 1. A2: Until tank level LIT01>R_WT_LT_CYC, Send DSX_PW_REQ = 0. Then start timer R_CYC_WASH_TM A3(after A2): SP1=R_PU_CIR_SPD, Delay R_PU_DELAY_TM, Then Start PU03. A4: WT_WASH_TIMES +1 A5:After R_CYC_WASH_TM elapsed, then stop PU03
T0600 | DRN_ELAP_TM elapsed and WT_WASH_TIMES>=R_WT_TIMES_SP
S0600 | SET_STATE | 设置状态 Set state | 0 | 0 | SP=0 | stop | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0% | 0 | 0 | 0 | STOP | MSG0: Change EM state A1: Change tank state to clean A2: Send DSX_PW_REQ= 0.
S0200 | CLOSE | 关闭EM Close EM | 0 | 0 | SP=0 | stop | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0% | 0 | 0 | 0 | STOP | MSG0: Close related EM.
S0300 | RELEASE | 释放EM Release EM | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | RELEASE | MSG0: Release related EM.
S7000 | HOLD | 暂停 pause | 0 | 0 | sp=0 | stop | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0 | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0 | 0-d | NA | 0% | 0-d | 0 | 0 | STOP | MSG0: All devices stopped. MSG1: Release all related devices. Disable all ForceSP&HM&SM&Timers
S8000 | CLOSE ALL | 关阀 Close all | 0 | 0 | sp=0 | stop | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0 | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0-d | 0 | 0-d | NA | 0% | 0-d | 0 | 0 | STOP | MSG0: Close all valves
Note:
a) | When REQ_PW =1, start CU_FB_TM until requie comfirmed, when CU_FB_TM elapsed, then hold.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max | REV.2a
| R_WT_LE_L | Yes | Wash tank low level | int | L | 50 | 1 | 1200
| R_DRN_ELAP_TM | Yes | Drain elapse time | real | min | 0.5 | 0 | 10
| R_PU_DRN_SPD | Yes | Pump Speed for pump drain | real | Hz | 25 | 15 | 50
| R_PU_CIR_SPD | Yes | Pump Speed for recirculation | real | Hz | 25 | 15 | 50
| R_PU_DELAY_TM | Yes | Pump delay time to start | int | sec | 20 | 1 | 60
| R_VLV_DELAY_TM | Yes | Valve delay open time | int | sec | 20 | 1 | 60
| R_VLV_PULSE_TM | Yes | Valve pulse open time | int | sec | 5 | 1 | 60
| R_WT_LT_CYC | Yes | Wash tank cycle level | real | L | 200 | 1 | 1200
| R_WT_TIMES_SP | Yes | Wash tank wash Times setpoint | int | NA | 1 | 1 | 10
| R_SELF_WASH_TM | Yes | Self Wash elapse time | real | min | 1 | 1 | 10
| R_CYC_WASH_TM | Yes | Pump cycle wash elapse time | real | min | 1 | 1 | 10
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Eng.Unit | Step | Begin | End
X
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Emergency Stop E-DSXCIP02 | X in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
13 | Indication Table
| Code |  | Description
| prompt |  | Step timer S130~170 elapsed