## Cover Sheet
Phase Specification PH_X_PUR_DF
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004200 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-30 | 吴婷 | Draft for review
| 0.1a | 2020-11-18 | 吴婷 | 1.ACTION TABILE 增加一个CM
| 0.1b | 2020-11-20 | 吴婷 | ACTION TABLE 删除CM,HOLD,ABORT顺控图修改
| 0.1c | 2020-12-10 | 吴婷 | HOLD Table新增
| 1.0 | 2021-03-03 | 吴婷 | 根据程序仿真修改
| 2.0 | 2021-04-26 | 吴婷 | 增加急停编号，删除效期参数。
| 2.0b | 2021-06-05 | 王树深 | 更新急停策略
| 2.0c | 2021-07-01 | 王树深 | 更新流量计量程范围
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase is used for transferring product from process tank to process tank with depth filtration and filter in the loop.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Process Equipment 无需信号交互 | DSX-DF03 | UF0301
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit | Equiment Module
| Process Equipment 无需信号交互 | EM_DF03
EM_DF03_FILT
EM's at other Units (Shared EM's)
| Unit | Equiment Module
| Process Tank(DPS) | EM_PUR_BOM | EM_PUR_PD_IN | EM_PUR_TOP
EM_PUR_FA1

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
转料过程中罐子控压，接收罐一直保压
根据泵转速来区分不同工艺

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
|  | Phase | EM
|  | Phase: PD_DF_FL CS_SEL_3: TA03_DF_TA04 | EM_DSXTA03_BOM | EM_DSXTA03_FA | EM_DSXDF03 | EM_FDSXDF0301 | EM_DSXTA04_PD_IN | EM_DSXTA04_TOP | EM_DSXTA04_FA
Step |  | Description | EM_PUR_BOM | EM_PUR_FA1 | EM_DF03 | EM_DF03_FILT | EM_PUR_PD_IN | EM_PUR_TOP | EM_PUR_FA1 | Report Record | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | MSG | 提示深层过滤DF03准备就绪，连接软管。准备完成后确认。 Operator message:DF03 ready,hose connected .please confirm when finish. | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1020 | PU_PRE | 延时以灌泵 Time delay for pump fill. | PD_OUT | PRESSURE_CONT | PD_IN | P_TS2 | PD1_TO_TK | PD_IN | VENT_FA | Record WT_DSXTA0401 | If PIT-DSXDF0301＞R_PT1_ALM，hold； If PIT-DSXDF0302＞R_PT2_ALM，hold； If PIT-DSXDF0303＞R_PT3_ALM，hold； If PIT-DSXDF0301-PIT-DSXDF0302 >R_DP1_ALM, hold; If PIT-DSXDF0302-PIT-DSXDF0303>R_DP2_ALM, hold | EM_DSXTA03_FA: SP=R_PT_SP1 △P=R_△P1 EM_DSXTA04_FA: SP=R_PT_SP2 △P=R_△P2
S1030 | PD_SUP | 物料转移到用点 Product supply to point of use | PD_OUT | PRESSURE_CONT | PD_IN_PU | P_TS2 | PD1_TO_TK | PD_IN | VENT_FA |  |  | EM_DSXTA03_FA: SP=R_PT_SP1 △P=R_△P1 EM_DSXTA04_FA: SP=R_PT_SP2 △P=R_△P2 Note1 |  | 恒流过滤,全程PID控制
S1040 | PU_STOP | 延时以停泵 Time delay for pump stop | PD_OUT | PRESSURE_CONT | PD_IN_PU | P_TS2 | PD1_TO_TK | PD_IN | VENT_FA |  |  | EM_DSXTA03_FA: SP=R_PT_SP1 △P=R_△P1 EM_DSXTA04_FA: SP=R_PT_SP2 △P=R_△P2
S1050 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | VENT_FA | Record WT_DSXTA0401 |  | EM_DSXTA04_FA: SP=R_PT_SP2 △P=R_△P2
S1060 | SET STATE | 重置状态 set state | CLOSE | VENT_FA | CLOSE | CLOSE | CLOSE | CLOSE | PRESSURE_CONT |  |  | EM_DSXTA04_FA: SP=R_PT_SP2 △P=R_△P2 | Source Tank=Dirty Target Tank = Process Line State = Dirty note 2 | DSX_DF03_X_TA04 note 2：状态不变
S7010 | HOLD | 暂停 pause | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD
S8010 | ABORT | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S8020 | SET_STATE | 重置状态 set state | CLOSE | VENT_FA | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  |  | Source Tank:Process Target Tank = Process Line State = Process
| Note1 | PU-DSXDF0301 speed control(PID control) by FIT-DSXDF0301

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_PT_SP1 | Yes | Process Tank TA03 pressure set point | int | barg | 0.5 | 0 | 3
| R_PT_SP1_DEV | NO | Process Tank TA03 pressure Deviation | real | barg | 0.1 | 0 | 1
| R_PT_SP2 | Yes | Process Tank TA04 pressure set point | real | barg | 0.5 | 0 | 3
| R_PT_SP2_DEV | NO | Process Tank TA04 pressure Deviation | real | barg | 0.1 | 0 | 1
| R_PU_PRE_TM | NO | Time delay for pump fill. | int | sec | 60 | 0 | 300
| R_WT_SP | Yes | TA03 Weight low level | int | kg | 3 | 0 | 1000
| R_ELAP_TM | NO | Time delay for tank empty. | int | sec | 10 | 0 | 100
| R_PU_STOP_TM | NO | Time delay for pump stop. | int | sec | 30 | 0 | 300
| R_FIC_SP | Yes | Flowrate set point | int | kg/h | 1500 | 0 | 18000
| R_PT1_ALM | NO | DF PI01 pressure for alarm | Real | barg | 3 | 0 | 5
| R_PT2_ALM | NO | DF PI02 pressure for alarm | Real | barg | 3 | 0 | 5
| R_PT3_ALM | NO | DF PI03 pressure for alarm | Real | barg | 3 | 0 | 5
| R_PT_ALM | Yes | Pipe pressure for alarm | int | barg | 3 | 0 | 3 | 每一个压力值2bar
| R_DP1_ALM | Yes | DF03 PI01-PI02 pressure for alarm | Real | barg | 3 | 0 | 5 | SP改成ALM
| R_DP2_ALM | Yes | DF03 PI02-PI03 pressure for alarm | Real | barg | 3 | 0 | 5
| R_FCV_SP | YES | Set point of control vavle opening | Real | % | 50 | 0 | 100
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description |  | Eng.Unit | Step | Begin | End
| L_FT_PV |  | Flowrate process value |  | kg/h
| L_WT_PV_DEV(Note 2) |  | Weight increase of collecting tank TA04 |  | kg
| L_PT1_PV |  | PIT_DSXDF0301 process value |  | barg
| L_PT2_PV |  | PIT_DSXDF0302 process value |  | barg
| L_PT3_PV |  | PIT_DSXDF0303 process value |  | barg
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR06/E-DSXPUR07 Emergency Stop
| Hold03 |  | WIT-DSXTA0401 fault
| Hold04 |  | PIT-DSXTA0301 fault
| Hold05 |  | PU-DSXDF0301 fault
| Hold06 |  | PIT-DSXDF0301 fault
| Hold07 |  | PIT-DSXDF0302 fault
| Hold08 |  | FIT-DSXDF0301 fault
| Hold09 |  | PIT-DSXDF0303 fault
| Hold10 |  | PIT-DSXTA0401 fault
Note 2：L_WT_PV_DEV is equal to WT_DSXTA0401 of S1050 minus WT_DSXTA0401 of S1020.