## Cover Sheet
Phase Specification
PH_X_HV
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004204 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-30 | 吴婷 | Draft for review
| 0.1a | 2020-11-18 | 吴婷 | 1.ACTION TABILE 增加一个CM； 2.配方参数表个别修改
| 0.1b | 2020-11-20 | 吴婷 | ACTION TABLE 删除CM,HOLD,ABORT顺控图修改
| 0.1c | 2020-12-10 | 吴婷 | HOLD Table新增,增加报警参数
| 1.0 | 2021-03-03 | 吴婷 | 根据程序仿真修改
| 2.0 | 2021-04-26 | 吴婷 | 增加急停编号，删除效期参数。
| 2.0b | 2021-06-02 | 王树深 | 增加上下游信号交互
| 2.0c | 2021-06-05 | 王树深 | 更新急停策略
| 2.0d | 2021-06-22 | 王树深 | 更新上下游信号交互策略
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase X_HV is used for transferring product from upstream to harvest tank .
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Process Tank(DPS) | 4000L HARVEST TANK UNIT TA02
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit | Equiment Module
| Process Tank(DPS) | EM_PUR_TOP
EM_PUR_FA2
EM_PUR_FA3
EM's at other Units (Shared EM's)
| Unit | Equiment Module
| N/A | N/A

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
开始条件：上游发送请求,此时开始控压（全程控压）
转料过程中一直保持微正压0.2
称重达到一定值，开启搅拌，侧壁进气
跳转条件:收到结束信号延时关闭阀门。

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
HOLD关闭阀门，控压，搅拌，通气还在。

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
|  | Phase | EM
|  | Phase: X_HV CS_SEL_1: UP_TO_TA02 | EM_DSXTA02_TOP | EM_DSXTA02_FA1 | EM_DSXTA02_FA2
Step |  | Description | EM_PUR_TOP | EM_PUR_FA2 | EM_PUR_FA3 | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A
S1010 | PD_TRS | 物料转移到用点 Product supply to point of use | PD_IN | VENT_FA | CLOSE |  | EM_DSXTA02_FA1: SP=R_PT_SP △P=R_△P | Confirm DSX_PD_Trans_Req=1， Send DSX_PD_Trans_Rdy3=1.
S1020 | AIR_IN | 罐子侧壁进气 Air in tank | PD_IN | VENT_FA | PA_TK | If FIT-DSXTA0201＞R_FIT_H_ALM,warning;If FIT-DSXTA0201＜R_FIT_L_ALM,warning | EM_DSXTA02_FA1: SP=R_PT_SP △P=R_△P EM_DSXTA02_FA2: FIC OUT =R_ FIT_SP
S1030 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | PRESSURE_CONT | PA_TK | If FIT-DSXTA0201＞R_FIT_H_ALM,warning;If FIT-DSXTA0201＜R_FIT_L_ALM,warning | EM_DSXTA02_FA1: SP=R_PT_SP △P=R_△P EM_DSXTA02_FA2: FIC OUT =R_ FIT_SP | Confirm DSX_PD_Trans_End=1,
S1040 | SET_STATE | 重置状态 set state | CLOSE | PRESSURE_CONT | PA_TK | If FIT-DSXTA0201＞R_FIT_H_ALM,warning;If FIT-DSXTA0201＜R_FIT_L_ALM,warning | EM_DSXTA02_FA1: SP=R_PT_SP △P=R_△P EM_DSXTA02_FA2: FIC OUT =R_ FIT_SP | Target Tank = Process Line State = Dirty
S7010 | HOLD | 暂停 pause | HOLD | PRESSURE_CONT | PA_TK | If FIT-DSXTA0201＞R_FIT_H_ALM,warning;If FIT-DSXTA0201＜R_FIT_L_ALM,warning | EM_DSXTA02_FA1: SP=R_PT_SP △P=R_△P EM_DSXTA02_FA2: FIC OUT =R_ FIT_SP
S8010 | ABORT | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE |  |  | Confirm DSX_PD_Trans_End=1, Send DSX_PD_Trans_Rdy=0
S8020 | SET_STATE | 重置状态 set state | CLOSE | CLOSE | CLOSE |  |  | Target Tank = Process Line State = Process

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_WT_SP | NO | Harvest tank TA02 minimum ventilation weight set point | real | kg | 2000 | 0 | 4000
| R_PT_SP | YES | Tank pressure set point | real | barg | 0.2 | 0 | 3
| R_PT_SP_DEV | NO | Deviation | real | barg | 0.05 | 0 | 1
| R_FIT_SP | YES | Flow of air through pipe | real | NL/min | 20 | 0 | 100
| R_SPEED_AG | YES | Speed of agitator | real | rpm | 150 | 0 | 300 | 恒速
| R_DELAY_TM | NO | Delay time for close valve | int | sec | 30 | 0 | 300
| R_FIT_H_WARN | YES | High flow of air for warn | real | NL/min | 50 | 0 | 999
| R_FIT_L_WARN | YES | Low flow of air for warn | real | NL/min | 2 | 0 | 20
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_PT_PV |  | Tank pressure process value |  | barg
| L_FIT_PV |  | Flow of air through pipe process value |  | L/min
| L_SPEED_AG_PV |  | Speed of agitator process value |  | rpm
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR06/E-DSXPUR07 Emergency Stop
| Hold03 |  | AG-DSXTA0201 fault
| Hold04 |  | PIT-DSXTA0201 fault
| Hold05 |  | WIT-DSXTA0201 fault
| Hold06 |  | FIT-DSXTA0201 fault
| Hold07 |  | DSX_PD_Alarm_Snd=1 or DSX_PD_Alarm_Rcv=1