## Cover Sheet
Phase Specification PH_C_PUR_CHT
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004206 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-30 | 吴婷 | Draft for review
| 0.1a | 2020-11-18 | 吴婷 | 1.ACTION TABLE 更新
| 0.1b | 2020-11-20 | 吴婷 | ACTION TABLE 个别命令修改
| 0.1c | 2020-12-10 | 吴婷 | 顺控图修改,电导和TOC同时检测
| 1.0 | 2021-03-03 | 吴婷 | 根据仿真测试修改； 根据FAT修改
| 2.0 | 2021-04-26 | 吴婷 | 增加急停编号
| 2.0b | 2021-06-05 | 王树深 | 修改PW清洗回罐和排放策略;修改prep medium时管道状态；修改急停策略
| 2.0c | 2021-06-17 | 王树深 | 增加参数
| 2.0d | 2021-06-28 | 王树深 | 修改S1020步EM_C_RTN的command为STOP
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase is used for CIP of transfer pipe from Process Tank to chromatography .
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Process Tank(DPS) | 4000L HARVEST TANK UNIT TA02
4000L PURIFICATION TANK UNIT TA04
4000L PURIFICATION TANK UNIT TA05
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit | Equiment Module
| Process Tank(DPS) | EM_PUR_HEAD
EM_PUR_CIPS1
EM_PUR_BOM
EM_PUR_PD_OUT
EM_PUR_CIPR
EM_PUR_CIPR_PU
EM's at other Units (Shared EM's)
| Unit | Equiment Module
| Process Equipment 都是DCS系统，内部交互 | EM_CHT_PD_IN
EM_CHT_BRK
EM_CHT_DRN
| CIP Station 都是DCS系统，内部交互 | EM_C_SUP
EM_C_CIP
EM_C_BTH
EM_C_RTN

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
Note1: | Current Medium will be judged by the logic,according to the parameter CIP_Medium1/CIP_Medium2/CIP_Medium3/CIP_Medium4
Note4 | Check CT and TOC simultaneously at the start of S1070.
For CHECK_CT:
1) If If AIT03 > R_WFI_CT_SP, then CHECK_CT=FAILED. If AIT03 < R_WFI_CT_SP, then enable Timer R_TM_CT.
2) If AIT03 < R_WFI_CT_SP and R_TM_CT is elapsed, then CHECK_CT=PASSED.
If AIT03 > R_WFI_CT_SP during R_TM_CT is elapsed, then CHECK_CT=FAILED.
For CHECK_TOC:
1) If QIT01 > R_WFI_TOC_SP, then CHECK_TOC=FAILED. QIT01 < R_WFI_TOC_SP, then enable Timer R_TM_TOC.
2) If QIT01 < R_WFI_TOC_SP and R_TM_TOC is elapsed, then CHECK_TOC=PASSED.
If QIT01 > R_WFI_TOC_SP during R_TM_TOC is elapsed, then CHECK_TOC=FAILED.
Alarm if CHECK_CT=FAILED or CHECK_TOC=FAILED.
预留TOC检测功能，该phase须能保证在无TOC检测的情况下正常运行。
Note3 | CHECK_CT and CHECK_TOC finished

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
|  | Phase | EM
|  | Phase: C_PUR_TO_CHT01 CS_SEL_1: TA02_TO_CHT01 | EM_DSXCHT01_PDIN | EM_DSXCHT01_BRK | EM_DSXCHT01_DRN | EM_DSXPUR_CIPS1 | EM_DSXTA02_HEAD | EM_DSXTA02_BOM | N/A | EM_DSXPUR_CIPR | EM_DSXPUR1CIPRPU | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DSXCIP02_RTN | EM_DSXCIP02_BTH
|  | Phase: C_PUR_TO_CHT02 CS_SEL_1: TA04_TO_CHT02 | EM_DSXCHT02_PDIN | EM_DSXCHT02_BRK | EM_DSXCHT02_DRN | EM_DSXPUR_CIPS1 | EM_DSXTA04_HEAD | EM_DSXTA04_BOM | N/A | EM_DSXPUR_CIPR | EM_DSXPUR1CIPRPU | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DSXCIP02_RTN | EM_DSXCIP02_BTH
|  | Phase: C_PUR_TO_CHT03 CS_SEL_1: TA05_TO_CHT03 | EM_DSXCHT03_PDIN | EM_DSXCHT03_BRK | EM_DSXCHT03_DRN | EM_DSXPUR_CIPS1 | EM_DSXTA05_HEAD | EM_DSXTA05_BOM | EM_DSXTA05_PDOUT | EM_DSXPUR_CIPR | EM_DSXPUR1CIPRPU | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DSXCIP02_RTN | EM_DSXCIP02_BTH
STEP |  | DESCRIPTION | EM_CHT_PD_IN | EM_CHT_BRK | EM_CHT_DRN | EM_PUR_CIPS1 | EM_PUR_HEAD | EM_PUR_BOM | EM_PUR_PD_OUT | EM_PUR_CIPR | EM_PUR_CIPR_PU | EM_C_CIP | EM_C_SUP | EM_C_RTN | EM_C_BTH | Report Record | Alarm Settings | Controller Settings | Other Actions
S9020 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9070 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9080 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | CHECK_MEDIUM | 检查CIP介质 Check CIP medium | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  | Assign value to Current_Medium according to the parameter CIP_Medium1/CIP_Medium2/CIP_Medium3/CIP_Medium4
S1020 | PREP_MEDIUM | 准备介质供应 Prepare medium to supply. | PD_IN_CIP | PD_PE_CIP | PE_CIPR | Note2 | CIP_PE | CIP_PE | Note3 | Note4 | CLOSE | Note1 | STOP | STOP | WT_FILTER_OPEN |  | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP1
S1030 | CIP_P | 清洗对象管道 CIP target pipe | PD_IN_CIP | PD_PE_CIP | PE_CIPR | Note2 | CIP_PE | CIP_PE | Note3 | Note4 | CLOSE | Note5 | MEDIUM_SUPPLY | Note7 | WT_FILTER_OPEN
S1040 | CHECK_CT_TOC | 电导和TOC检测 Check CT and TOC | PD_IN_CIP | PD_PE_CIP | PE_CIPR | Note2 | CIP_PE | CIP_PE | Note3 | Note4 | CLOSE | SUPPLY_WFI | MEDIUM_SUPPLY | RTN_TOC | WT_FILTER_OPEN | Record AIT03 Record QIT01 |  |  | If Medium is WFI, record AIT03 and QIT01 at the start of S1040. Record result of S1040: CHECK_CT=PASSED or FAILED CHECK_TOC=PASSED or FAILED
S1060 | STOP_PUMP | 泵关闭 Supply pump off | PD_IN_CIP | PD_PE_CIP | PE_CIPR | Note2 | CIP_PE | CIP_PE | Note3 | Note4 | CLOSE | STOP | STOP | Note7 | WT_FILTER_OPEN
S1070 | BLOW_P | 吹扫排放目标管道 Blow target pipe to drain | PD_IN_CIP | PD_PE_CIP | PE_CIPR | Note2 | CIP_PE | CIP_PE | Note3 | Note4 | CLOSE | STOP | AIR_BLOW | Note8 | WT_FILTER_OPEN
S1080 | FINAL_CHECK | 最终介质检查 Final check the medium | PD_IN_CIP | PD_PE_CIP | PE_CIPR | Note2 | CIP_PE | CIP_PE | Note3 | Note4 | CLOSE | STOP | STOP | Note7 | WT_FILTER_OPEN
S1090 | BLOW_LP | 开启低点并吹扫排放目标管道 Blow target pipe to drian with opening the low point valves | PD_IN_CIP | PD_CIP_DRN | PE_CIPR_PUL_DRN | Note2 | CIP_PE | CIP_PE_PUL_DRN | Note3 | Note4 | PU_OFF_DRN | STOP | AIRBLOW_LP | RTN_LP_DR | WT_FILTER_OPEN
S1100 | CLOSE | 关闭所有设备 Close all device | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | STOP | STOP | STOP |  |  |  | If CHECK_CT&CHECK_TOC=PASSED, go to S1110. If CHECK_CT&CHECK_TOC=FAILED, end the phase.
S1110 | SET_STATE | 重置状态 set state | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | STOP | STOP | STOP |  |  |  | set state to clean
S7010 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD |  |  |  | First close EM_C_CIP and EM_PUR_CIPR_PU then close other EM
S8010 | ABORT | 中止步骤 Abort | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | STOP | STOP | STOP |  |  |  | First close EM_C_CIP and EM_PUR_CIPR_PU then close other EM
S8020 | SET_STATE | 重置状态 set state | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | STOP | STOP | STOP | STOP |  |  |  | set state to dirty
| Phase | Note2 | Note3 | Note4
| Phase: C_PUR_TO_CHT01 CS_SEL_1: TA02_TO_CHT01 | N/A | N/A | CIPR_FR_CHT01
| Phase: C_PUR_TO_CHT02 CS_SEL_1: TA04_TO_CHT02 | CIP_TO_TA04 | N/A | CIPR_FR_CHT02
| Phase: C_PUR_TO_CHT03 CS_SEL_1: TA05_TO_CHT03 | CIP_TO_TA05 | PD_OUT3 | CIPR_FR_CHT03
| Note1 | If medium is PW, use PREP_PW If medium is ALKALI, use PREP_ALK If medium is WFI,use PREP_WFI
| Note5 | If medium is PW, use SUPPLY_PW If medium is ALKALI, use SUPPLY_ALK If medium is WFI,use SUPPLY_WFI
| Note6 | If medium is PW ,use RTN_DR_NP; If medium is ALKALI, use RTN_TK. If medium is WFI, use RTN_TOC.
| Note7 | If medium is PW is CIP_Medium1, use RTN_DR_NP;If medium is CIP_Medium3,,use RTN_DR. If medium is ALKALI, use RTN_TK. If medium is WFI, use RTN_TOC.
| Note8 | If medium is PW is CIP_Medium1, use RTN_DR_NP;If medium is CIP_Medium3,use RTN_TK. If medium is ALKALI, use RTN_TK. If medium is WFI, use RTN_TOC.
Note on E23: 作者: 因层析变更而引起的修改，蓝色填充

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| CIP_MEDIUM1 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_MEDIUM2 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_MEDIUM3 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_MEDIUM4 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| R_MAX_TM_STEP1 | NO | Maximum step execution time,hold if exceed the time | real | min | 30 | 0 | 120
| R_TM_CIP_PW | NO | CIP time for pipe | real | min | 5 | 0 | 60
| R_TM_CIP_ALK | NO | CIP time for pipe | real | min | 8 | 0 | 60
| R_TM_CIP_WFI | YES | CIP time for pipe | real | min | 5 | 0 | 60
| R_TM_BLOW_PW | YES | Blow time after PW flush | real | min | 5 | 0 | 10
| R_TM_BLOW_ALK | YES | Blow time after ALK flush | real | min | 5 | 0 | 10
| R_TM_BLOW_WFI | YES | Blow time after WFI flush | real | min | 5 | 0 | 10
| R_TM_BLOW_LP | YES | Blow time after WFI flush | real | min | 5 | 0 | 10
| R_WFI_CT_SP | YES | Qualified CT | real | µS/cm | 5 | 0 | 5
| R_TM_CT | NO | Conductivity check duration | int | sec | 60 | 0 | 600
| R_TM_TOC | NO | TOC check duration | int | sec | 60 | 0 | 600
| R_WFI_TOC_SP | YES | TOC judgment setpoint | real | ppb | 1000 | 0 | 2000
| R_SPD_SUP_PU | YES | Speed of supply pump | real | Hz | 30 | 0 | 50
| R_ALK_TEMP | YES | Alkali temperature | real | °C | 80 | 0 | 100
| R_ALK_TM | YES | Alkali preparation time | int | sec | 20 | 0 | 500
| R_ALK_PRE_CT | YES | Alkali preparation CT | real | mS/cm | 18 | 0 | 30
`
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description |  | Eng.Unit | Step | Begin | End
| L_WFI_CT_PV |  | Process value of conductivity recorded | real | µS/cm | 1040
| L_WFI_TOC_PV |  | Process value of TOC check | real | ppb | 1040
| L_CT_CHECK |  | CHECK_CT is PASSED or FAILED | Nameset | N/A | 1040
| L_TOC_CHECK |  | CHECK_TOC is PASSED or FAILED | Nameset | N/A | 1040
| FE-DSXCIP0201 |  | CIP supply pump flowrate curve | real | m3/h
| AIT-DSXCIP0203 |  | Conductivity curve during WFI flush | real | µS/cm
| QIT-DSXCIP0201 |  | TOC curve during WFI flush | real | ppb
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR06/E-DSXPUR07/E-DSXCIP02 Emergency Stop
| Hold03 |  | CIP Station fault
| Hold04 |  | R_MAX_TM_STEP1 is elapsed