## Cover Sheet
Phase Specification _PH_C_POU_DIS_DS2_4
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-011021 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-30 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-30 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_.....
| Step | max. 16 characters, _ for delimiter
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 1.0 | 2021-03-18 | 杜林茂 | 新增
| 2.0 | 2021-04-12 | 杜林茂 | 增加急停编号
| 2.0b | 2021-06-05 | 王树深 | 修改prep medium时管道状态；修改急停策略
| 2.0c | 2021-06-17 | 王树深 | 增加参数
| 2.0d | 2021-06-28 | 王树深 | 修改S1020EM_BH_DIS_DRN_B 的command为CLOSE
| 3.0 | 2021-07-30 | 王树深 | 根据1/2线SAT更新

## Description
6. | Description
The Phase is used for CIP of buffer transfer line from point of use to buffer distribution valves
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Process Tank(DPS) | 4000L PURIFICATION TANK UNIT TA03
4000L PURIFICATION TANK UNIT TA04
| Process Equipment | HPLC #1 WORK UNIT CHT01
HPLC #2 WORK UNIT CHT02
HPLC #3 WORK UNIT CHT03
| Process Equipment | DEPTH FILTRATION UNIT DF03
NF WORK UNIT NF01
| 超滤 | UF/DF WORK UNIT UF01 for Line 2 and 4
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at Own Units
| Unit | Equiment Module
| Process Tank (DPS) | EM_PUR_HEAD
EM_PUR_CIPS1
EM_PUR_CIPS2
EM_CHT_CIP_IN
EM_CHT_CIP
EM_PUR_PD_IN
EM_DF04
EM_DF03
EM_UF_SHARED
EM_CHT_BRK
EM's at other Units (Shared EM's)
| Unit | Equiment Module
| BH Tank | EM_BH_HEAD
EM_BUF_CIPS
EM_BH_BOM
EM_BH_DIS
EM_BH_POU
EM_BH_DIS_DRN_B
| CIP Station | EM_C_CIP
EM_C_SUP
EM_C_BTH
EM_BCIP_CIPS

## SFC_CHECK
8. | RUN Logic with Check Steps
| Note2: | R_SELECT_STATION is 03 or 05. Default of R_SELECT_STATION can be modified.
If R_SELECT_STATION is 03, select CIP03 if CIP03 is standby. Select CIP05 if CIP03 is occupied.

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN
8. | RUN Logic without Check Steps
Note1: | Current Medium will be judged by the logic,according to the parameter CIP_Medium1/CIP_Medium2/CIP_Medium3/CIP_Medium4

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
Action Table
The following actions will be performed during the stepwise phase execution
| PH_C_CHT_DIS | R_C_CHT01_DIS_SEL1 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DS1CIP02_BTH | N/A | EM_DSXPUR_CIPS1 | N/A | N/A | N/A | EM_DSXCHT01CIPIN | EM_DSXCHT01CIPW | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA20_CHT01 | EM_DSXBHDISDRNB2 | N/A | EM_DSXCHT01_BRK
|  | R_C_CHT01_DIS_SEL2 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DS1CIP02_BTH | N/A | EM_DSXPUR_CIPS1 | N/A | N/A | N/A | EM_DSXCHT01CIPIN | EM_DSXCHT01CIPST | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA26_CHT01 | EM_DSXBHDISDRNB2 | N/A | EM_DSXCHT01_BRK
|  | R_C_CHT01_DIS_SEL3 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DS1CIP02_BTH | N/A | EM_DSXPUR_CIPS1 | N/A | N/A | N/A | EM_DSXCHT01CIPIN | EM_DSXCHT01CIPAL | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA32_CHT01 | EM_DSXBHDISDRNB2 | N/A | EM_DSXCHT01_BRK
|  | R_C_CHT02_DIS_SEL1 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DS1CIP02_BTH | N/A | EM_DSXPUR_CIPS1 | N/A | N/A | N/A | EM_DSXCHT02CIPIN | EM_DSXCHT02CIPW | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA20_CHT02 | EM_DSXBHDISDRNB2 | N/A | EM_DSXCHT02_BRK
|  | R_C_CHT02_DIS_SEL2 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DS1CIP02_BTH | N/A | EM_DSXPUR_CIPS1 | N/A | N/A | N/A | EM_DSXCHT02CIPIN | EM_DSXCHT02CIPST | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA26_CHT02 | EM_DSXBHDISDRNB2 | N/A | EM_DSXCHT02_BRK
|  | R_C_CHT02_DIS_SEL3 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DS1CIP02_BTH | N/A | EM_DSXPUR_CIPS1 | N/A | N/A | N/A | EM_DSXCHT02CIPIN | EM_DSXCHT02CIPAL | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA32_CHT02 | EM_DSXBHDISDRNB2 | N/A | EM_DSXCHT02_BRK
|  | R_C_CHT03_DIS_SEL1 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DS1CIP02_BTH | N/A | EM_DSXPUR_CIPS1 | N/A | N/A | N/A | EM_DSXCHT03CIPIN | EM_DSXCHT03CIPW | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA20_CHT03 | EM_DSXBHDISDRNB4 | N/A | EM_DSXCHT03_BRK
|  | R_C_CHT03_DIS_SEL2 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DS1CIP02_BTH | N/A | EM_DSXPUR_CIPS1 | N/A | N/A | N/A | EM_DSXCHT03CIPIN | EM_DSXCHT03CIPST | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA26_CHT03 | EM_DSXBHDISDRNB4 | N/A | EM_DSXCHT03_BRK
|  | R_C_CHT03_DIS_SEL3 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DS1CIP02_BTH | N/A | EM_DSXPUR_CIPS1 | N/A | N/A | N/A | EM_DSXCHT03CIPIN | EM_DSXCHT03CIPAL | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA32_CHT03 | EM_DSXBHDISDRNB4 | N/A | EM_DSXCHT03_BRK
| PH_PUR_DIS | R_C_TA03_DIS_SEL | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note13) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | N/A | N/A | N/A | EM_DSXBH4_CIPS | N/A | N/A | EM_DSXTA21_HEAD | EM_DSXTA21_BOM | N/A | EM_DSXTA03_PD_IN | N/A | N/A | EM_DSXTA20_TA03 | EM_DSXBHDISDRNB3 | N/A | N/A
|  | R_C_TA04_DIS_SEL | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note13) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | N/A | N/A | N/A | EM_DSXBH2_CIPS | N/A | N/A | EM_DSXTA29_HEAD | EM_DSXTA29_BOM | N/A | EM_DSXTA04_PD_IN | N/A | N/A | EM_DSXTA20_TA04 | EM_DSXBHDISDRNB3 | N/A | N/A
| PH_C_DSZ_UF | R_C_UF01_DIS_SEL1 | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note13) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | N/A | EM_DSXPUR_CIPS2 | EM_DSXTA08_HEAD | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSZTA20_UF01 | EM_DSXBHDISDRNB1 | EM_DSZUF01SHARED | N/A
|  | R_C_UF01_DIS_SEL2 | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note13) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | N/A | EM_DSXPUR_CIPS2 | EM_DSXTA08_HEAD | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSZTA26_UF01 | EM_DSXBHDISDRNB1 | EM_DSZUF01SHARED | N/A
|  | R_C_UF01_DIS_SEL3 | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note13) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | N/A | EM_DSXPUR_CIPS2 | EM_DSXTA08_HEAD | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSZTA32_UF01 | EM_DSXBHDISDRNB1 | EM_DSZUF01SHARED | N/A
| PH_C_VF_DIS | R_C_VF01_DIS_SEL | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note13) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | N/A | N/A | N/A | EM_DSXBH4_CIPS | N/A | N/A | EM_DSXTA30_HEAD | EM_DSXTA30_BOM | EM_DSXTA30_DIS | N/A | EM_DSXDF04 | N/A | EM_DSXTA20_VF01 | EM_DSXBHDISDRNB4 | N/A | N/A
| PH_C_DF_DIS | R_C_DF03_DIS_SEL | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note13) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | N/A | N/A | N/A | EM_DSXBH4_CIPS | N/A | N/A | EM_DSXTA21_HEAD | EM_DSXTA21_BOM | N/A | N/A | N/A | EM_DSXDF03 | EM_DSXTA20_DF03 | EM_DSXBHDISDRNB2 | N/A | N/A
Step |  | Description | EM_C_CIP | EM_C_SUP | EM_C_BTH | EM_BCIP_CIPS | EM_PUR_CIPS1 | EM_PUR_CIPS2 | EM_PUR_HEAD | EM_BUF_CIPS | EM_CHT_CIP_IN | EM_CHT_CIP | EM_BH_HEAD | EM_BH_BOM | EM_BH_DIS | EM_PUR_PD_IN | EM_DF04 | EM_DF03 | EM_BH_POU | EM_BH_DIS_DRN_B | EM_UF_SHARED | EM_CHT_BRK | Alarm Settings | Controller Settings | Other Actions
S9000 | STATION_CHECK | 检查CIP站的占用状态 Check the occupation of CIP stations. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | MESSAGE | 提示是否放弃 Prompt to abort the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | STATE_CHECK | 状态检查 Check all line and vessel status | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ROUTE_CHECK | 路径检查 Check if all the jumpers are in right position | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9070 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9080 | ENABLE HM&SM | 启动程序监测 Enable hold monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | CHECK_MEDIUM | 检查CIP介质 Check CIP medium | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Assign value to Current_Medium according to the parameter CIP_Medium1/CIP_Medium2/CIP_Medium3/CIP_Medium4
S1020 | PREP_MEDIUM | 准备供应CIP介质 Prepare to supply CIP medium | Note4 | STOP | WT_FILTER_OPEN | Note6 | Note7 | Note8 | CIP_UF | Note9 | CIP_IN | ALW_IN_CIP | CIP_PE | CIP_PE | TA30 _TO_ TA06UF02 | CIP_PE_WFI | WFI_CIP | WFI_CIP | C_S_POU_TO_DIS | CLOSE | Note10 | CLOSE | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP
S1030 | CIP_P | 清洗对象管道 CIP target pipe | Note5 | MEDIUM_SUPPLY | WT_FILTER_OPEN | Note6 | Note7 | Note8 | CIP_UF | Note9 | CIP_IN | ALW_IN_CIP | CIP_PE | CIP_PE | TA30 _TO_ TA06UF02 | CIP_PE_WFI | WFI_CIP | WFI_CIP | C_S_POU_TO_DIS | CIP_DRN | Note10 | CLOSE
S1040 | STOP_PUMP | 泵关闭 Supply pump off | STOP_PUMP | MEDIUM_SUPPLY | WT_FILTER_OPEN | Note6 | Note7 | Note8 | CIP_UF | Note9 | CIP_IN | ALW_IN_CIP | CIP_PE | CIP_PE | TA30 _TO_ TA06UF02 | CIP_PE_WFI | WFI_CIP | WFI_CIP | C_S_POU_TO_DIS | CIP_DRN | Note10 | CLOSE
S1050 | BLOW_P | 吹扫排放目标管道 Blow target pipe to drain | STOP | AIR_BLOW | WT_FILTER_OPEN | Note6 | Note7 | Note8 | CIP_UF | Note9 | CIP_IN | ALW_IN_CIP | CIP_PE | CIP_PE | TA30 _TO_ TA06UF02 | CIP_PE_WFI | WFI_CIP | WFI_CIP | C_S_POU_TO_DIS | CIP_DRN | Note10 | CLOSE
S1060 | FINAL_CHECK | 最终介质检查 Final check the medium | STOP | STOP | WT_FILTER_OPEN | Note6 | Note7 | Note8 | CIP_UF | Note9 | CIP_IN | ALW_IN_CIP | CIP_PE | CIP_PE | TA30 _TO_ TA06UF02 | CIP_PE_WFI | WFI_CIP | WFI_CIP | C_S_POU_TO_DIS | CIP_DRN | Note10 | CLOSE
S1070 | BLOW_LP | 开启低点并吹扫排放目标管道 Blow target pipe to drian with opening the low point valves | STOP | AIRBLOW_LP | WT_FILTER_OPEN | Note6 | Note7 | Note8 | CIP_UF | Note9 | CIP_IN | ALW_IN_CIP | CIP_PE | CIP_P_PUL_DR | TA30 _TO_ TA06UF02 | CIP_PE_WFI | WFI_CIP | WFI_CIP | C_S_POU_TO_DIS | CIP_DRN | Note10 | BUF_CIP_DRN
S1080 | CLOSE | 关闭所有设备 Close all device | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S1090 | SET_STATE | 状态设置 Set statge | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Set state to CLEAN
S7010 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD |  |  | First to HOLD EM_C_CIP, then ohrers
S8010 | ABORT | 中止步骤 Abort | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | First to STOP EM_C_CIP, then ohrers
S8020 | SET_STATE | 状态设置 Set statge | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Set state to DIRTY
Note1: If select CIP03 station, EM will be EM_DSXCIP03. If select CIP05 station, EM will be EM_DSXCIP05.
| Note2: If select CIP03 station, EM will be EM_DSXCIP03_SUP. If select CIP05 station, EM will be EM_DSXCIP05_SUP. | [6 empty] | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
| Note3: If select CIP03 station, EM will be EM_DSXCIP03_CIPS. If select CIP05 station, EM will be EM_DSXCIP05_CIPS. | [6 empty] | "Y" in "DSY" represents Line number. "Y" can be 1, 3.
| Note4: If medium is PW, use PREP_PW. If medium is CAU, use PREP_ALK. If medium is WFI, use PREP_WFI. | [6 empty] | "Z" in "DSZ" represents Line number. "Z" can be 2, 4.
Note5: If medium is PW, use SUPPLY_PW. If medium is CAU, use SUPPLY_ALK. If medium is WFI, use SUPPLU_WFI.
Note13: If select CIP03 station, EM will be EM_DSXCIP03_BTH. If select CIP05 station, EM will be EM_DSXCIP05_BTH.
|  |  | Note6 | Note7 | Note8 | Note9 | Note10
| PH_C_CHT_DIS | R_C_CHT01_DIS_SEL1 | N/A | CIP_TO_CHT01 | N/A | N/A | N/A
|  | R_C_CHT01_DIS_SEL2 | N/A | CIP_TO_CHT01 | N/A | N/A | N/A
|  | R_C_CHT01_DIS_SEL3 | N/A | CIP_TO_CHT01 | N/A | N/A | N/A
|  | R_C_CHT02_DIS_SEL1 | N/A | CIP_TO_CHT02 | N/A | N/A | N/A
|  | R_C_CHT02_DIS_SEL2 | N/A | CIP_TO_CHT02 | N/A | N/A | N/A
|  | R_C_CHT02_DIS_SEL3 | N/A | CIP_TO_CHT02 | N/A | N/A | N/A
|  | R_C_CHT03_DIS_SEL1 | N/A | CIP_TO_CHT03 | N/A | N/A | N/A
|  | R_C_CHT03_DIS_SEL2 | N/A | CIP_TO_CHT03 | N/A | N/A | N/A
|  | R_C_CHT03_DIS_SEL3 | N/A | CIP_TO_CHT03 | N/A | N/A | N/A
| PH_PUR_DIS | R_C_TA03_DIS_SEL | CIP_TO_TA17 | N/A | N/A | CIP_TO_TA21 | N/A
|  | R_C_TA04_DIS_SEL | CIP_TO_TA31 | N/A | N/A | CIP_TO_TA29 | N/A
| PH_C_DSZ_UF | R_C_UF01_DIS_SEL1 | CIP_TO_TA08 | N/A | CIP_TO_UF01 | N/A | WFI_IN_CIP
|  | R_C_UF01_DIS_SEL2 | CIP_TO_TA08 | N/A | CIP_TO_UF01 | N/A | STORAGE_IN_CIP
|  | R_C_UF01_DIS_SEL3 | CIP_TO_TA08 | N/A | CIP_TO_UF01 | N/A | CIP_IN_CIP
| PH_C_VF_DIS | R_C_VF01_DIS_SEL | CIP_TO_TA17 | N/A | N/A | CIP_TO_TA30 | N/A
| PH_C_DF_DIS | R_C_DF03_DIS_SEL | CIP_TO_TA17 | N/A | N/A | CIP_TO_TA21 | N/A

## ALARM (hidden)
INDICATION | S150~S180

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| CIP_MEDIUM1 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_MEDIUM2 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_MEDIUM3 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| CIP_MEDIUM4 | NO | CIP skid supply medium | N/A | N/A | PW ALKALI WFI NONE | N/A | N/A
| R_CHT_DIS_SEL | YES | CIP route from CHT01 to TA20 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from CHT01 to TA26 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from CHT01 to TA32 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from CHT02 to TA20 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from CHT02 to TA26 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from CHT02 to TA32 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from CHT03 to TA20 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from CHT03 to TA26 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from CHT03 to TA32 | N/A | N/A | N/A | N/A | N/A
| R_DSZ_UF_SEL | YES | CIP route from UF01 to TA20 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from UF01 to TA26 | N/A | N/A | N/A | N/A | N/A
|  | YES | CIP route from UF01 to TA32 | N/A | N/A | N/A | N/A | N/A
| R_SELECT_STATION | NO | Preferred CIP Station selected | N/A | N/A | CIP03 or CIP05 | N/A | N/A
| R_MAX_TM_STEP | NO | Maximum step execution time,hold if exceed the time | real | min | 30 | 0 | 120
| R_TM_CIP_PW | NO | CIP time for pipe | real | min | 5 | 0 | 60
| R_TM_CIP_ALK | NO | CIP time for pipe | real | min | 8 | 0 | 60
| R_TM_CIP_WFI | YES | CIP time for pipe | real | min | 5 | 0 | 60
| R_TM_BLOW_PW | YES | Blow time after PW flush | real | min | 5 | 0 | 10
| R_TM_BLOW_ALK | YES | Blow time after ALK flush | real | min | 5 | 0 | 10
| R_TM_BLOW_WFI | YES | Blow time after WFI flush | real | min | 5 | 0 | 10
| R_TM_BLOW_LP | YES | Blow time after WFI flush | real | min | 5 | 0 | 10
| R_SPD_SUP_PU | YES | Speed of supply pump | int. | Hz | 30 | 0 | 50
| R_ALK_TEMP | YES | Alkali temperature | real | °C | 80 | 0 | 100
| R_ALK_TM | YES | Alkali preparation time | int. | sec | 20 | 0 | 500
| R_ALK_PRE_CT | YES | Alkali preparation CT | real | mS/cm | 18 | 0 | 30
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSZPUR01/E-DSZPUR02/E-DSZPUR03/E-DSZPUR04//E-DSZPUR06/E-DSZPUR07/E-DSZBH01/E-DSZCIP02 Emergency Stop
| Hold03 |  | CIP station Hold
| Hold04 |  | R_MAX_TM_STEP elapsed
13 | Indication Table
| Code |  | Description
| prompt |  | Step timer S130~170 elapsed