## Cover Sheet
Phase Specification
PH_S_CHT_PUR
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004218 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-21 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-21 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-31 | 王树深 | Draft for review
| 0.1a | 2020-11-18 | 王树深 | 1.SFC_RUN中S1030-S1200D的判断条件中SIP_SET_TT改为R_SIP_TT_SP。 2.ParameterHold Tables中R_JC_HEAT_TT_SP参数删掉。 3.Action Table中15行增加Controller Settings： SP:EM_PUR_CS/PIC OUT= CS_PT_SP1
| 0.1b | 2020-11-20 | 王树深 | 1.SFC_RUN中REHEAT前的判断条件中SIP_SET_TT - R_△TT改为R_SIP_TT_SP -R_SIP_TT_SP_DEV。同时在ParameterHold Tables表中R_△TT替换为R_PRS_PT_SP_DEV。 2.Action Table和ParameterHold Tables中参数R_PRS_PT_SP1和R_PRS_PT_SP1用R_PRS_PT_SP和R_PRS_PT_SP_DEV替换。 3.Action Table中EM_PUR_PA调用的commend有部分修改，EM_PUR_CS的commend在release步骤改为CLOSE。
| 0.1C | 2020-12-10 | 王树深 | 部分commands修改
| 1.0 | 2021-03-03 | 王树深 | 程序仿真修改
| 2.0 | 2021-04-26 | 王树深 | 增加急停编号
| 2.0b | 2021-06-05 | 王树深 | 更新急停策略
| 2.0c | 2021-06-13 | 王树深 | 修改hold逻辑和参数描述
| 3.0 | 2021-07-21 | 王树深 | 根据SAT修改

## Description
6. | Description
The PhasePH_S_CHT_PUR is used for Sterilization of tank with cooling by chilled water; tank heated by plant steam 1. Monitoring of all condensate temperatures in sterilization step and resetting of sterilization timer if one of the temperatures drop SIP_TT_SP.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Process Equipment | DSXCHT01
DSXCHT02
DSXCHT03
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Process Tank(DPS) | EM_PUR_PD_IN
EM_PUR_CS
EM_PUR_PA
EM_PUR_HEAD
EM_PUR_TOP
| Process Equipment | EM_CHT_PD_OUT

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
| Unit class | Phase | TT(Note1):
| Process Tank(DPS) | S_DSXC01_TO_T03 | TT-DSXCHT0102 | TT-DSXTA0305
|  | S_DSXC02_TO_T05 | TT-DSXCHT0202 | TT-DSXTA0505
|  | S_DSXC03_TO_T06 | TT-DSXCHT0302 | TT-DSXTA0605

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note7: R_SIP_TM in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase（Note8） |  |  | EM
Process Tank(DPS) |  | S_DSXC01_TO_T03 | EM_DSXCHT01_PDOUT | EM_DSXTA03_PD_IN | EM_DSXPUR_CS1 | EM_DSXPUR_PA | EM_DSXTA02_HEAD | EM_DSXTA03_TOP
|  | S_DSXC02_TO_T05 | EM_DSXCHT02_PDOUT | EM_DSXTA05_PD_IN | EM_DSXPUR_CS1 | EM_DSXPUR_PA | EM_DSXTA04_HEAD | EM_DSXTA05_TOP
|  | S_DSXC03_TO_T06 | EM_DSXCHT03_PDOUT | EM_DSXTA06_PD_IN | EM_DSXPUR_CS1 | EM_DSXPUR_PA | EM_DSXTA05_HEAD | EM_DSXTA06_TOP
Step |  | Description | EM_CHT_PD_OUT | EM_PUR_PD_IN | EM_PUR_CS | EM_PUR_PA | EM_PUR_HEAD | EM_PUR_TOP | Alarm Settings | Controller Settings | Other Actions | REV.2 | 删除EM
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | PE_HEAT | 管道通入纯蒸汽加热，打开排放旁路，排除凝水，管道继续升温。 Heat pipe by clean steam and drain condensate water by bypass valve. | PD_OUT_SIP | PD1_TO_TK | CS_SUPPLY | CLOSE | SIP_CHT_OUT | SIP_PD_IN_BPS1 |  | SP: EM_PUR_CS/PIC OUT= R_CS_PT_SP1
S1020 | HEAT | 管道通入纯蒸汽加热，只通过疏水阀排除凝水，管道继续升温。 Heat pipe by clean steam and drain by steam trap valve. | PD_OUT_SIP | PD1_TO_TK | CS_SUPPLY | CLOSE | SIP_CHT_OUT | SIP_PD_IN_PE1 | Enable "Step time hold" if TT <HEAT_TT_SP when Step_Timer is over | SP: EM_PUR_CS/PIC OUT= R_CS_PT_SP2
S1030 | STERILIZE | 灭菌计时 Sterilize timer. | PD_OUT_SIP | PD1_TO_TK | CS_SUPPLY | CLOSE | SIP_CHT_OUT | SIP_PD_IN_PE1
S1040 | COOL | 通过呼吸器向管道通入压缩空气，并且冷凝排放旁路打开，进行冷却。 Cool pipe by pressure air. | PD_OUT_SIP | PD1_TO_TK | CLOSE | PA_PE | SIP_CHT_OUT | SIP_PD_IN_BPS1 | Enable "Step time hold" if TT >COOL_TT_SP_1 when Step_Timer is over
S1050 | PRESS_HOLD | 管道保压。 Pipe keep pressure at set point. | PD_OUT_SIP | PD1_TO_TK | CLOSE | PA_PE | SIP_CHT_OUT | CLOSE
S1060 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S1070 | SET_STATE | 设置状态 Set the state | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Set State to SIPed
S1200 | REHEAT | 重新加热通过加入纯蒸汽。 Reheat pipe by into clean stean. | PD_OUT_SIP | PD1_TO_TK | CS_SUPPLY | CLOSE | SIP_CHT_OUT | SIP_PD_IN_PE1
S7000 | HOLD | 暂停 pause | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD
S8020 | COOL | 通过呼吸器向管道通入压缩空气，并且冷凝排放旁路打开，进行冷却。 Cool pipe by pressure air. | PD_OUT_SIP | PD1_TO_TK | CLOSE | PA_PE | SIP_CHT_OUT | SIP_PD_IN_BPS1 | Enable "Step time hold" if TT >COOL_TT_SP_1 when Step_Timer is over |  | Release EM: EM_PUR_CS
S8060 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | N/A | CLOSE | CLOSE | CLOSE
S8070 | SET_STATE | 状态变更 Set State | CLOSE | CLOSE | N/A | CLOSE | CLOSE | CLOSE |  |  | Set State as 'CLEAN'
Note8："X" in "DSX" represents Line number. "X" can be 1,2, 3,4.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max | REV.2a
| R_CS_PT_SP1 | YES | Steam pressure set point for pre-heating pipe | real | bar(g) | 1.6 | 0 | 2.5
| R_CS_PT_SP2 | YES | Steam pressure set point for sterilize pipe | real | bar(g) | 1.5 | 0 | 2.5
| R_S1010_STEP_TM | NO | maximum pre-heating time,alarm if exceed the time | real | min | 2 | 1 | 100
| R_S1020_STEP_TM | NO | maximum heating time,alarm if exceed the time | real | min | 30 | 5 | 100
| R_S1040_STEP_TM | NO | maximum cooling time,alarm if exceed the time | real | min | 60 | 1 | 100
| R_PRESS_HOLD_TM | YES | Keep pressure in pipe after SIP | real | min | 1 | 0 | 5
| R_SIP_TM | YES | SIP time | real | min | 15 | 0 | 60
| R_STABLE_TM | NO | Stable timer | real | min | 2 | 0 | 10
| R_HEAT_TT_SP | YES | temperature set point for vessel pre-heating | real | °C | 95 | 80 | 100
| R_SIP_TT_SP | YES | SIP control temperature | real | °C | 123 | 121 | 125
| R_COOL_TT_SP_1 | YES | temperature set point for COOL_VESSEL_1 | real | °C | 60 | 0 | 110 | delete PRESSURE_SP_D_4
| R_SIP_TT_SP_DEV | NO | SIP temperature Deviation | real | °C | 2 | 0 | 99
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_SIP_TM |  | SIP time | real | min
| L_SIP_TT_PV |  | SIP control temperature | real | °C
| L_COOL_TT_PV_1 |  | Temperature for COOL_VESSEL_1 | real | °C
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR06/E-DSXPUR07 Emergency Stop
| Hold03 |  | Step timer S1010,1020,1040 elapsed
| Hold04 |  | Any TT fault
13 | Indication Table
| Code |  | Description
| prompt |  | Step timer S130~170 elapsed

## ALARM (hidden)
INDICATION | S150~S180