## Cover Sheet
Phase Specification
PH_S_PUR_CHT
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004219 |  | 3.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-07-21 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-07-21 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-31 | 王树深 | Draft for review
| 0.1a | 2020-11-18 | 王树深 | 1.SFC_RUN中S1030-S1200D的判断条件中SIP_SET_TT改为R_SIP_TT_SP。
| 0.1b | 2020-11-20 | 王树深 | 1.SFC_RUN中REHEAT前的判断条件中SIP_SET_TT - R_△TT改为R_SIP_TT_SP -R_SIP_TT_SP_DEV。同时在ParameterHold Tables表中R_△TT替换为R_PRS_PT_SP_DEV。 2.Action Table和ParameterHold Tables中参数R_PRS_PT_SP1和R_PRS_PT_SP1用R_PRS_PT_SP和R_PRS_PT_SP_DEV替换。 3.Action Table中EM_PUR_PA调用的commend有部分修改，EM_PUR_CS的commend在release步骤改为CLOSE。 4.ParameterHold Tables中补充参数R_S8060_ELAP_TM。 5.SFC_RUN中note2和note5增加TT-DSXTA0403，TT-DSXTA0503.
| 0.1c | 2020-12-10 | 王树深 | 部分commands修改及增加EM_PUR_PS，参数的修改补充。
| 1.0 | 2021-03-03 | 王树深 | 程序仿真修改
| 2.0 | 2021-04-26 | 王树深 | 增加急停编号
| 2.0b | 2021-06-02 | 王树深 | 增加上下游信号交互
| 2.0c | 2021-06-05 | 王树深 | 更新急停策略
| 2.0d | 2021-06-22 | 王树深 | 释放罐子单独SIP，罐子管道一起SIP时PUR_PA的EM;更新疏水策略；
| 3.0 | 2021-07-21 | 王树深 | 根据SAT升版

## Description
6. | Description
The Phase PH_S_PUR_CHT is used for Sterilization of tank with cooling by chilled water; tank heated by plant steam 1. Monitoring of all condensate temperatures in sterilization step and resetting of sterilization timer if one of the temperatures drop SIP_TT_SP.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Process Tank(DPS) | DSXTA02
DSXTA04
DSXTA05
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Process Tank(DPS) | EM_PUR_CS
EM_PUR_PA
EM_PUR_HEAD
EM_PUR_TOP
EM_PUR_FA1
EM_PUR_FA2
EM_PUR_FA3
EM_PUR_PS
EM_PUR_JC
EM_PUR_BOM
EM_PUR_PD_OUT
| Process Equipment | EM_CHT_PD_IN
EM_CHT_BRK
EM_CHT_DRN

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
| Unit class | Phase | TT(Note1): | TT(Note2): |  |  |  |  | PT(Note3): | TT(Note4): |  | TT(Note5): | [5 empty] | PT(Note6):
| Process Tank(DPS) | S_DSXT02_TO_C01 | TIT-DSXTA0201 | TIT-DSXTA0201 | TT-DSXTA0202 | TT-DSXTA0203 | TT-DSXTA0208 | TT-DSXBIO(Note10) | PIT-DSXTA0201 | TT-DSXTA0202 | TT-DSXCHT0101 | TIT-DSXTA0201 | TT-DSXTA0202 | TT-DSXTA0203 | TT-DSXTA0208 | TT-DSXBIO(Note10) | TT-DSXCHT0101 | PIT-DSXTA0201
|  | S_DSXT04_TO_C02 | TIT-DSXTA0401 | TIT-DSXTA0401 | TT-DSXTA0402 | TT-DSXTA0403 | N/A | N/A | PIT-DSXTA0401 | TT-DSXTA0402 | TT-DSXCHT0201 | TIT-DSXTA0401 | TT-DSXTA0402 | TT-DSXTA0403 | N/A | N/A | TT-DSXCHT0201 | PIT-DSXTA0401
|  | S_DSXT05_TO_C03 | TIT-DSXTA0501 | TIT-DSXTA0501 | TT-DSXTA0502 | TT-DSXTA0503 | N/A | N/A | PIT-DSXTA0501 | TT-DSXTA0502 | TT-DSXCHT0301 | TIT-DSXTA0501 | TT-DSXTA0502 | TT-DSXTA0503 | N/A | N/A | TT-DSXCHT0301 | PIT-DSXTA0501
Note10:This TT only uesd for CS_SEL1 or CS_SEL3.

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note7: R_SIP_TM in RUN shall be reset when RESTART.
x

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase（Note9） | EM
Process Tank(DPS) |  | S_DSXPUR02_CHT01:SEL1 | EM_DSXPUR_CS1 | N/A | EM_DSXTA02_HEAD | EM_DSXTA02_TOP | N/A | EM_DSXTA02_FA1 | EM_DSXTA02_FA2 | EM_DSXPUR_PS | EM_DSXTA02_JC | EM_DSXTA02_BOM | N/A | N/A | N/A | N/A
|  | S_DSXPUR02_CHT01:SEL2 | EM_DSXPUR_CS1 | EM_DSXPUR_PA | EM_DSXTA02_HEAD | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA02_BOM | N/A | EM_DSXCHT01_PDIN | EM_DSXCHT01_BRK | EM_DSXCHT01_DRN
|  | S_DSXPUR02_CHT01:SEL3 | EM_DSXPUR_CS1 | N/A | EM_DSXTA02_HEAD | EM_DSXTA02_TOP | N/A | EM_DSXTA02_FA1 | EM_DSXTA02_FA2 | EM_DSXPUR_PS | EM_DSXTA02_JC | EM_DSXTA02_BOM | N/A | EM_DSXCHT01_PDIN | EM_DSXCHT01_BRK | EM_DSXCHT01_DRN
|  | S_DSXPUR04_CHT02:SEL1 | EM_DSXPUR_CS1 | N/A | EM_DSXTA04_HEAD | EM_DSXTA04_TOP | EM_DSXTA04_FA | N/A | N/A | EM_DSXPUR_PS | EM_DSXTA04_JC | EM_DSXTA04_BOM | N/A | N/A | N/A | N/A
|  | S_DSXPUR04_CHT02:SEL2 | EM_DSXPUR_CS1 | EM_DSXPUR_PA | EM_DSXTA04_HEAD | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA04_BOM | N/A | EM_DSXCHT02_PDIN | EM_DSXCHT02_BRK | EM_DSXCHT02_DRN
|  | S_DSXPUR04_CHT02:SEL3 | EM_DSXPUR_CS1 | N/A | EM_DSXTA04_HEAD | EM_DSXTA04_TOP | EM_DSXTA04_FA | N/A | N/A | EM_DSXPUR_PS | EM_DSXTA04_JC | EM_DSXTA04_BOM | N/A | EM_DSXCHT02_PDIN | EM_DSXCHT02_BRK | EM_DSXCHT02_DRN
|  | S_DSXPUR05_CHT03:SEL1 | EM_DSXPUR_CS1 | N/A | EM_DSXTA05_HEAD | EM_DSXTA05_TOP | EM_DSXTA05_FA | N/A | N/A | EM_DSXPUR_PS | EM_DSXTA05_JC | EM_DSXTA05_BOM | N/A | N/A | N/A | N/A
|  | S_DSXPUR05_CHT03:SEL2 | EM_DSXPUR_CS1 | EM_DSXPUR_PA | EM_DSXTA05_HEAD | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA05_BOM | EM_DSXTA05_PDOUT | EM_DSXCHT03_PDIN | EM_DSXCHT03_BRK | EM_DSXCHT03_DRN
|  | S_DSXPUR05_CHT03:SEL3 | EM_DSXPUR_CS1 | N/A | EM_DSXTA05_HEAD | EM_DSXTA05_TOP | EM_DSXTA05_FA | N/A | N/A | EM_DSXPUR_PS | EM_DSXTA05_JC | EM_DSXTA05_BOM | EM_DSXTA05_PDOUT | EM_DSXCHT03_PDIN | EM_DSXCHT03_BRK | EM_DSXCHT03_DRN
Step |  | Description | EM_PUR_CS | EM_PUR_PA | EM_PUR_HEAD | EM_PUR_TOP | EM_PUR_FA1 | EM_PUR_FA2 | EM_PUR_FA3 | EM_PUR_PS | EM_PUR_JC | EM_PUR_BOM | EM_PUR_PD_OUT | EM_CHT_PD_IN | EM_CHT_BRK | EM_CHT_DRN | Alarm Settings | Controller Settings | Other Actions | REV.2 | 删除EM
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Send DSX_HV_OCC_Req=1, Confirm DSX_HV_OCC_Rdy=1(Note11)
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | JC_DRAIN | SIP之前夹套排空 Jacket drain before SIP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | JC_DRN | CLOSE | N/A | N/A | N/A | N/A
S1020 | JC_HEAT | 夹套通入工业蒸汽辅助加热罐体 Heat tank by industrial steam into jacket. | CLOSE | CLOSE | CLOSE | CLOSE | VENT_FA | VENT_FA | CLOSE | PS_SUPPLY | JC_HEAT | CLOSE | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT <JC_HEAT_TT_SP when Step_Timer is over
S1030 | HEAT_1 | 罐体通入纯蒸汽加热，打开排放旁路，排除凝水，罐体继续升温。 Heat tank by clean steam into tank and drain condensate water by bypass valve. | CS_SUPPLY | CLOSE | SIP_TK | SIP_TK | SIP_FA | SIP_FA | SIP_FA | PS_SUPPLY | JC_HEAT | SIP_TK_HEAT | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT <HEAT_TT_SP when Step_Timer is over | SP: EM_PUR_CS/PIC OUT= R_CS_PT_SP1
S1040 | HEAT_2 | 罐体通入纯蒸汽加热，只通过疏水阀排除凝水，罐体继续升温。 Heat tank by clean steam into tank and drain by steam trap valve. | CS_SUPPLY | CLOSE | SIP_TK | SIP_TK | SIP_FA | SIP_FA | SIP_FA | CLOSE | CLOSE | SIP_TK | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT <SIP_TT_SP when Step_Timer is over | SP: EM_PUR_CS/PIC OUT= R_CS_PT_SP2 | Release EM: EM_PUR_PS
S1050 | STERILIZE | 灭菌计时 Sterilize timer. | CS_SUPPLY | CLOSE | SIP_TK | SIP_TK | SIP_FA | SIP_FA | SIP_FA | N/A | CLOSE | SIP_TK | N/A | N/A | N/A | N/A
S1060 | REPLACE_AIR | 罐子空气置换 Replace the Air of Vessel | CLOSE | CLOSE | CLOSE | CLOSE | PA_TK | PA_TK | SIP_FA | N/A | CLOSE | SIP_TK_HEAT | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT >COOL_TT_SP_1 when Step_Timer is over |  | Release EM: EM_PUR_CS，EM_PUR_HEAD
S1070 | COOL_1 | 夹套通低流量冷却介质降温罐子 Cool Vessel by Low Flow of Water | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | CLOSE | N/A | JC_COOL_PUL | SIP_TK | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT >COOL_TT_SP_2 when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S1080 | COOL_2 | 夹套通高流量冷却介质降温罐子 Cool Vessel by High Flow of Water | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | CLOSE | N/A | JC_COOL | SIP_TK | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT >COOL_TT_SP_3 when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S1090 | PRESS_HOLD | 罐体保压。 Tank keep pressure at set point. | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | CLOSE | N/A | JC_BW_BK | CLOSE | N/A | N/A | N/A | N/A | Enable "Step time hold" if PT <PRS_PT_SP when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S1100 | JC_DRAIN | SIP之后夹套排空 Jacket drain after SIP | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | CLOSE | N/A | JC_DRN | CLOSE | N/A | N/A | N/A | N/A |  | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S1110 | CLOSE | 关闭所有阀门 Close all valve. | N/A | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE | N/A | N/A | N/A | N/A |  |  | Send DSX_HV_OCC_Req=0（Note11）
S1120 | SET_STATE | 设置状态 Set the state | N/A | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE | N/A | N/A | N/A | N/A |  |  | Set State to SIPed
S1200 | REHEAT | 重新加热通过加入纯蒸汽。 Reheat tank by into clean stean. | CS_SUPPLY | CLOSE | SIP_TK | SIP_TK | SIP_FA | SIP_FA | SIP_FA | N/A | CLOSE | SIP_TK | N/A | N/A | N/A | N/A
S2010 | PE_HEAT | 管道通入纯蒸汽加热，打开排放旁路，排除凝水，管道继续升温。 Heat pipe by clean steam and drain condensate water by bypass valve. | CS_SUPPLY | CLOSE | SIP_PE | N/A | N/A | N/A | N/A | N/A | N/A | SIP_PE_HEAT | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP_BPS |  | SP: EM_PUR_CS/PIC OUT= R_CS_PT_SP1
S2030 | HEAT | 管道通入纯蒸汽加热，只通过疏水阀排除凝水，罐体继续升温。 Heat pipe by clean steam and drain by steam trap valve. | CS_SUPPLY | CLOSE | SIP_PE | N/A | N/A | N/A | N/A | N/A | N/A | SIP_PE | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP | Enable "Step time hold" if TT <HEAT_TT_SP when Step_Timer is over | SP: EM_PUR_CS/PIC OUT= R_CS_PT_SP2
S2050 | STERILIZE | 灭菌计时 Sterilize timer. | CS_SUPPLY | CLOSE | SIP_PE | N/A | N/A | N/A | N/A | N/A | N/A | SIP_PE | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP
S2060 | COOL | 通过呼吸器向管道通入压缩空气，并且冷凝排放旁路打开，进行冷却。 Cool pipe by pressure air. | CLOSE | PA_PE | SIP_PE | N/A | N/A | N/A | N/A | N/A | N/A | SIP_PE_HEAT | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP_BPS | Enable "Step time hold" if TT >COOL_TT_SP_4 when Step_Timer is over
S2080 | PRESS_HOLD | 管道保压。 Pipe keep pressure at set point. | CLOSE | PA_PE | SIP_PE | N/A | N/A | N/A | N/A | N/A | N/A | PR_PE | PD_OUT3 | PD_IN_PR | CLOSE | CLOSE
S2110 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | N/A | N/A | N/A | N/A | N/A | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Send DSX_HV_OCC_Req=0（Note11）
S2120 | SET_STATE | 设置状态 Set the state | CLOSE | CLOSE | CLOSE | N/A | N/A | N/A | N/A | N/A | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Set State to SIPed
S2200 | REHEAT | 重新加热通过加入纯蒸汽。 Reheat pipe by into clean stean. | CS_SUPPLY | CLOSE | SIP_PE | N/A | N/A | N/A | N/A | N/A | N/A | SIP_PE | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP
S3010 | JC_DRAIN | SIP之前夹套排空 Jacket drain before SIP | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | JC_DRN | N/A | N/A | N/A | N/A | N/A
S3020 | JC_HEAT | 夹套通入工业蒸汽辅助加热罐体 Heat tank by industrial steam into jacket. | N/A | CLOSE | CLOSE | CLOSE | VENT_FA | VENT_FA | CLOSE | PS_SUPPLY | JC_HEAT | N/A | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT <JC_HEAT_TT_SP when Step_Timer is over
S3030 | HEAT_1 | 罐体和管道通入纯蒸汽加热，打开排放旁路，排除凝水，罐体继续升温。 Heat tank and pipe by clean steam into tank and drain condensate water by bypass valve. | CS_SUPPLY | CLOSE | SIP_TKP | SIP_TKP | SIP_FA | SIP_FA | SIP_FA | PS_SUPPLY | JC_HEAT | SIP_TKP_HEAT | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP_BPS | Enable "Step time hold" if TT <HEAT_TT_SP when Step_Timer is over | SP: EM_PUR_CS/PIC OUT= R_CS_PT_SP1
S3040 | HEAT_2 | 罐体和管道通入纯蒸汽加热，只通过疏水阀排除凝水，罐体继续升温。 Heat tank and pipe by clean steam into tank and drain by steam trap valve. | CS_SUPPLY | CLOSE | SIP_TKP | SIP_TKP | SIP_FA | SIP_FA | SIP_FA | CLOSE | CLOSE | SIP_TKP | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP | Enable "Step time hold" if TT <SIP_TT_SP when Step_Timer is over | SP: EM_PUR_CS/PIC OUT= R_CS_PT_SP2 | Release EM:EM_PUR_PS
S3050 | STERILIZE | 灭菌计时 Sterilize timer. | CS_SUPPLY | CLOSE | SIP_TKP | SIP_TKP | SIP_FA | SIP_FA | SIP_FA | N/A | CLOSE | SIP_TKP | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP
S3060 | REOLACE_AIR | 罐子和管道空气置换 Replace the Air of Vessel and pipe | CLOSE | CLOSE | CLOSE | CLOSE | PA_TK | PA_TK | PA_TK | N/A | CLOSE | SIP_TKP_HEAT | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP_BPS | Enable "Step time hold" if TT >COOL_TT_SP_1 when Step_Timer is over |  | Release EM EM_PUR_CS，EM_PUR_HEAD
S3070 | COOL_1 | 夹套通低流量冷却介质降温罐子 Cool Vessel by Low Flow of Water | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | SIP_FA | N/A | JC_COOL_PUL | SIP_TKP | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP | Enable "Step time hold" if TT >COOL_TT_SP_2 when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S3080 | COOL_2 | 夹套通高流量冷却介质降温罐子 Cool Vessel by High Flow of Water | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | SIP_FA | N/A | JC_COOL | SIP_TKP | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP | Enable "Step time hold" if TT >COOL_TT_SP_3 when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S3090 | PRESS_HOLD | 罐体和管道保压。 Tank and pipe keep pressure at set point. | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | CLOSE | N/A | JC_BW_BK | PR_TKP | PD_OUT3 | PD_IN_PR | CLOSE | CLOSE | Enable "Step time hold" if PT <PRS_PT_SP when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S3100 | JC_DRAIN | SIP之后夹套排空 Jacket drain after SIP | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | CLOSE | N/A | JC_DRN | PR_TKP | PD_OUT3 | PD_IN_PR | CLOSE | CLOSE |  | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S3110 | CLOSE | 关闭所有阀门。 Close all valve. | N/A | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Send DSX_HV_OCC_Req=0（Note11）
S3120 | SET_STATE | 设置状态 Set the state | N/A | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Set State to SIPed
S3200 | REHEAT | 重新加热通过加入纯蒸汽。 Reheat tank by into clean stean. | CS_SUPPLY | CLOSE | SIP_TKP | SIP_TK | SIP_FA | SIP_FA | SIP_FA | N/A | CLOSE | SIP_TKP | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP
S7000 | HOLD(Note8) | 暂停 pause | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD
S8010 | REPLACE_AIR | 罐子空气置换 Replace the Air of Vessel | CLOSE | CLOSE | CLOSE | CLOSE | PA_TK | PA_TK | PA_TK | CLOSE | CLOSE | SIP_TK_HEAT | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT >COOL_TT_SP_1 when Step_Timer is over |  | Release EM: EM_PUR_CS ， EM_PUR_PS， EM_PUR_HEAD
S8020 | COOL_1 | 夹套通低流量冷却介质降温罐子 Cool Vessel by Low Flow of Water | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | PA_TK | N/A | JC_COOL_PUL | SIP_TK | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT >COOL_TT_SP_2 when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S8030 | COOL_2 | 夹套通高流量冷却介质降温罐子 Cool Vessel by High Flow of Water | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | PA_TK | N/A | JC_COOL | SIP_TK | N/A | N/A | N/A | N/A | Enable "Step time hold" if TT >COOL_TT_SP_3 when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S8040 | JC_DRAIN | SIP之后夹套排空 Jacket drain after SIP | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | PA_TK | N/A | JC_BW_BK | SIP_TK | N/A | N/A | N/A | N/A |  | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S8050 | COOL | 通过呼吸器向管道通入压缩空气，并且冷凝排放旁路打开，进行冷却。 Cool pipe by pressure air. | CLOSE | PA_PE | SIP_PE | N/A | N/A | N/A | N/A | N/A | N/A | SIP_PE_HEAT | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP_BPS | Enable "Step time hold" if TT >COOL_TT_SP_4 when Step_Timer is over
S8060 | REPLACE_AIR | 罐子和管道空气置换 Replace the Air of Vessel and pipe | CLOSE | CLOSE | CLOSE | CLOSE | PA_TK | PA_TK | PA_TK | CLOSE | CLOSE | SIP_TKP_HEAT | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP_BPS | Enable "Step time hold" if TT >COOL_TT_SP_1 when Step_Timer is over |  | Release EM: EM_PUR_CS， EM_PUR_PS， EM_PUR_HEAD
S8070 | COOL_1 | 夹套通低流量冷却介质降温罐子 Cool Vessel by Low Flow of Water | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | SIP_FA | N/A | JC_COOL_PUL | SIP_TKP | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP | Enable "Step time hold" if TT >COOL_TT_SP_2 when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S8080 | COOL_2 | 夹套通高流量冷却介质降温罐子 Cool Vessel by High Flow of Water | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | SIP_FA | N/A | JC_COOL | SIP_TKP | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP | Enable "Step time hold" if TT >COOL_TT_SP_3 when Step_Timer is over | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S8090 | JC_DRAIN | SIP之后夹套排空 Jacket drain after SIP | N/A | CLOSE | N/A | CLOSE | PRESSURE_CONT | PRESSURE_CONT | CLOSE | N/A | JC_BW_BK | SIP_TKP | PD_OUT3 | PD_IN_SIP | PD_PE_SIP | PE_SIP |  | SP: EM_PUR_FA_PIT01*=PT(Note3); EM_PUR_FA1/SP=R_PRS_PT_SP; EM_PUR_FA1/△P=R_PRS_PT_SP_DEV; EM_PUR_FA2/SP=R_PRS_PT_SP; EM_PUR_FA2/△P=R_PRS_PT_SP_DEV
S8101 | CLOSE | 关闭所有阀门。 Close all valve. | N/A | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE | N/A | N/A | N/A | N/A |  |  | Send DSX_HV_OCC_Req=0（Note11）
S8102 | CLOSE | 关闭所有阀门。 Close all valve. | N/A | CLOSE | CLOSE | N/A | N/A | N/A | N/A | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Send DSX_HV_OCC_Req=0（Note11）
S8103 | CLOSE | 关闭所有阀门。 Close all valve. | N/A | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Send DSX_HV_OCC_Req=0（Note11）
S8110 | SET_STATE(Note8) | 状态变更 Set State | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | N/A | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | Set State as 'CLEAN'
Note8， If phase is S_DSXPUR02_CHT01:SEL1，need enable EM_DSXPUR_CS1，EM_DSX_PUR_PA，EEM_DSXTA02_HEAD，EM_DSXTA02_TOP，EM_DSXTA02_FA1，EM_DSXTA02_FA2，EM_DSXPUR_PS，EM_DSXTA02_JC，EM_DSXTA02_BOM； If phase is S_DSXPUR02_CHT01:SEL2，need enable EM_DSXPUR_CS1，EM_DSX_PUR_PA，EEM_DSXTA02_HEAD，EM_DSXTA02_BOM，EM_DSXCHT01_PDIN，EM_DSXCHT01_BRK，EM_DSXCHT01_DRN； If phase is S_DSXPUR02_CHT01:SEL3，need enable EM_DSXPUR_CS1，EM_DSX_PUR_PA，EEM_DSXTA02_HEAD，EM_DSXTA02_TOP，EM_DSXTA02_FA1，EM_DSXTA02_FA2，EM_DSXPUR_PS，EM_DSXTA02_JC，EM_DSXTA02_BOM，EM_DSXCHT01_PDIN，EM_DSXCHT01_BRK，EM_DSXCHT01_DRN； If phase is S_DSXPUR04_CHT02:SEL1，need enable EM_DSXPUR_CS1，EM_DSX_PUR_PA，EEM_DSXTA04_HEAD，EM_DSXTA04_TOP，EM_DSXTA04_FA，EM_DSXPUR_PS，EM_DSXTA04_JC，EM_DSXTA04_BOM； If phase is S_DSXPUR04_CHT02:SEL2，need enable EM_DSXPUR_CS1，EM_DSX_PUR_PA，EEM_DSXTA04_HEAD，EM_DSXTA04_BOM，EM_DSXCHT02_PDIN，EM_DSXCHT02_BRK，EM_DSXCHT02_DRN； If phase is S_DSXPUR04_CHT02:SEL3，need enable EM_DSXPUR_CS1，EM_DSX_PUR_PA，EEM_DSXTA04_HEAD，EM_DSXTA04_TOP，EM_DSXTA04_FA，EM_DSXPUR_PS，EM_DSXTA04_JC，EM_DSXTA04_BOM，EM_DSXCHT02_PDIN，EM_DSXCHT02_BRK，EM_DSXCHT02_DRN； If phase is S_DSXPUR05_CHT03:SEL1，need enable EM_DSXPUR_CS1，EM_DSX_PUR_PA，EEM_DSXTA05_HEAD，EM_DSXTA05_TOP，EM_DSXTA05_FA1，EM_DSXTA05_FA2，EM_DSXPUR_PS，EM_DSXTA05_JC，EM_DSXTA05_BOM； If phase is S_DSXPUR05_CHT03:SEL2，need enable EM_DSXPUR_CS1，EM_DSX_PUR_PA，EEM_DSXTA05_HEAD，EM_DSXTA05_BOM，EM_DSXTA05_PDOUT，EM_DSXCHT03_PDIN，EM_DSXCHT03_BRK，EM_DSXCHT03_DRN； If phase is S_DSXPUR05_CHT03:SEL3，need enable EM_DSXPUR_CS1，EM_DSX_PUR_PA，EEM_DSXTA05_HEAD，EM_DSXTA05_TOP，EM_DSXTA05_FA1，EM_DSXTA05_FA2，EM_DSXPUR_PS，EM_DSXTA05_JC，EM_DSXTA05_BOM，EM_DSXTA05_PDOUT，EM_DSXCHT03_PDIN，EM_DSXCHT03_BRK，EM_DSXCHT03_DRN；
Note9："X" in "DSX" represents Line number. "X" can be 1,2, 3,4.
Not11：This signal interaction only uesd for S_DSXPUR02_CHT01:SEL1 or S_DSXPUR02_CHT01:SEL3.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_CS_SEL | NO | SEL1:SIP only for TANK | Name Set | N/A | 1 | 0 | 99
|  |  | SEL2:SIP only for PIPE | Name Set | N/A | 2 | 0 | 99
|  |  | SEL3:SIP for PIPE and TANK | Name Set | N/A | 3 | 0 | 99
| R_S1010_ELAP_TM | NO | Jacket drain time | real | min | 2 | 1 | 100
| R_S1020_STEP_TM | NO | maximum jacket-heating time,alarm if exceed the time | real | min | 30 | 5 | 100
| R_S1030_STEP_TM | NO | maximum pre-heating time of tank,alarm if exceed the time | real | min | 30 | 5 | 100
| R_S1040_STEP_TM | NO | maximum heating time of tank,alarm if exceed the time | real | min | 30 | 5 | 100
| R_S1060_STEP_TM | NO | maximum pre-cooling time of tank,alarm if exceed the time | real | min | 10 | 1 | 100
| R_S1070_STEP_TM | NO | maximum jacket low flow cooling time,alarm if exceed the time | real | min | 30 | 1 | 100
| R_S1080_STEP_TM | NO | maximum jacket high flow cooling time,alarm if exceed the time | real | min | 30 | 1 | 100
| R_S1100_ELAP_TM | NO | Jacket drain time | real | min | 2 | 1 | 100
| R_S2010_STEP_TM | NO | maximum pre-heating time of pipe,alarm if exceed the time | real | min | 2 | 1 | 100
| R_S2030_STEP_TM | NO | maximum heating time of pipe,alarm if exceed the time | real | min | 30 | 5 | 100
| R_S2060_STEP_TM | NO | maximum pre-cooling time of tank,alarm if exceed the time | real | min | 60 | 1 | 100
| R_S3010_ELAP_TM | NO | Jacket drain time | real | min | 2 | 1 | 100
| R_S3020_STEP_TM | NO | maximum jacket-heating time,alarm if exceed the time | real | min | 30 | 5 | 100
| R_S3030_STEP_TM | NO | maximum pre-heating time of tank and pipe,alarm if exceed the time | real | min | 30 | 5 | 100
| R_S3040_STEP_TM | NO | maximum heating time of tank and pipe,alarm if exceed the time | real | min | 30 | 5 | 100
| R_S3060_STEP_TM | NO | maximum pre-cooling time of tank and pipe,alarm if exceed the time | real | min | 10 | 1 | 100
| R_S3070_STEP_TM | NO | maximum jacket low flow cooling time,alarm if exceed the time | real | min | 30 | 1 | 100
| R_S3080_STEP_TM | NO | maximum jack high flow cooling time,alarm if exceed the time | real | min | 30 | 1 | 100
| R_S3100_ELAP_TM | NO | Jacket drain time | real | min | 2 | 1 | 100
| R_S8040_ELAP_TM | NO | Jacket drain time | real | min | 5 | 1 | 100
| R_S8090_ELAP_TM | NO | Jacket drain time | real | min | 5 | 1 | 100
| R_SIP_TM | YES | SIP time | real | min | 15 | 0 | 60
| R_STABLE_TM | NO | Stable time | real | min | 2 | 0 | 10
| R_PRESS_HOLD_TM | YES | Keep pressure in pipe after SIP | real | min | 1 | 0 | 5
| R_CS_PT_SP1 | YES | Steam pressure set point for pre-heating | real | barg | 1.8 | 0 | 2.5
| R_CS_PT_SP2 | YES | Steam pressure set point for sterilize | real | barg | 1.7 | 0 | 2.5
| R_JC_HEAT_TT_SP | YES | temperature set point for vessel jacket heating | real | °C | 40 | 30 | 100
| R_HEAT_TT_SP | YES | temperature set point for vessel pre-heating | real | °C | 95 | 80 | 100
| R_SIP_TT_SP | YES | SIP control temperature | real | °C | 123 | 121 | 125
| R_COOL_TT_SP_1 | YES | temperature set point for COOL_1 | real | °C | 100 | 0 | 110
| R_COOL_TT_SP_2 | YES | temperature set point for COOL_2 | real | °C | 95 | 0 | 110
| R_COOL_TT_SP_3 | YES | temperature set point for COOL_3 | real | °C | 60 | 0 | 110
| R_COOL_TT_SP_4 | YES | temperature set point for COOL_4 | real | °C | 60 | 0 | 110
| R_SIP_TT_SP_DEV | NO | SIP temperature Deviation | real | °C | 2 | 0 | 99
| R_PRS_PT_SP | YES | Final pressure set point for tank pressurization | real | barg | 0.5 | 0 | 1.5
| R_PRS_PT_SP_DEV | YES | Final pressure deviation set point for tank pressurization | real | barg | 0.2 | 0 | 1.5
| R_JC_BLOW_TM | YES | Jacket blowing time for GLW return | real | min | 5 | 0 | 100
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description |  | Eng.Unit | Step | Begin | End
| L_SIP_TM |  | SIP time | real | min
| L_SIP_TT_PV |  | SIP control temperature | real | °C
| L_COOL_TT_PV_1 |  | Temperature for COOL_VESSEL_1 | real | °C
| L_COOL_TT_PV_2 |  | Temperature for COOL_VESSEL_2 | real | °C
| L_COOL_TT_PV_3 |  | Temperature for COOL_VESSEL_3 | real | °C
| L_PRS_PT_PV |  | Pressure for tank Pressurization | real | barg
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR06/E-DSXPUR07 Emergency Stop
| Hold03 |  | Step timer S1020,1030,1040,1060,1070,1080,2010,2030,2060,3020,3030,3040,3060,3070,3080 elapsed
| Hold04 |  | Any TT fault
13 | Indication Table
| Code |  | Description
| prompt |  | Step timer S130~170 elapsed

## ALARM (hidden)
INDICATION | S150~S180